TENDER DOCUMENT

# EASTERN POWER DISTRIBUTION COMPANY OF AP LTD (APEPDCL)

REQUEST FOR SELECTION OF EMPANELMENT FOR DESIGN,SUPPLY, INSTALLATION, TESTING & COMMISSIONING and Integrated Comprehensive Maintenance for 5 Years of Grid Connected Rooftop Solar Photovoltaic (PV) Power Units of capacity 1 KWp to 10 KWp for Residential sector in APEPDCL.

UNDER

CAPEX MODE

TENDER NOTICE NO:

RFS No. 01/2020-21, Dated.02.12.2020

CLOSING DATE       06.01.2021 at 15.00 hrs

Issued by

Eastern Power Distribution Company of AP Ltd

Corporate Office, P&T, Colony, Seethammadhara, Visakhapatnam, Visakhapatnam District,

Tel: 0891 -2853776/764/771; E-mail: cgm_ec@apeasternpower.com, solar@apeasternpower.com

# DISCLAIMER

- The Tender document is not transferable.

- This Tender is issued by Eastern Power Distribution Company of AP Ltd (APEPDCL).

- The Bid document is not a prospectus or offer on invitation to the public in relation to the sale of shares, debentures or securities, nor shall this Bid document or any part of it form the basis of or be relied upon in any way in connection with, any contract relating to any shares, debentures or securities.

- In considering a response to this Tender, each recipient should make its own independent assessment and seek its own professional, technical, financial and legal advice.

- Whilst the information in this Tender document has been prepared in good faith, it is not and does not purport to be comprehensive or to have been independently verified. Neither APEPDCL nor any of their officers or employees, nor any of their advisers nor consultants, accept any liability or responsibility for the accuracy, reasonableness or completeness of, or for any errors, omissions or misstatements, negligent or otherwise, relating to the proposed Project, or makes any representation or warranty, express or implied, with respect to the information contained in this document or on which this document is based or with respect to any written or oral information made or to be made available to any of the recipients or their professional advisers and, so far as permitted by law and except in the case of fraudulent misrepresentation by the party concerned, and liability therefore is hereby expressly disclaimed.

- The information contained in this document is selective and is subject to updating, expansion, revision and amendment issued before due date. It does not, and does not purport to, contain all the information that a recipient may require. Neither APEPDCL nor any of their officers, employees nor any of its advisors nor consultants undertakes to provide any recipient with access to any additional information or to update the information in this document or to correct any inaccuracies therein which may become apparent. Each recipient must conduct its own analysis of the information contained in this document or to correct any inaccuracies therein that may be contained in this document and is advised to carry out its own investigation in relation to the Project(s)/Tender, the legislative and regulatory regime which applies thereto and by and all matters pertinent to the proposed Project/Tender and to seek its own professional advice on the legal, financial, regulatory and taxation consequences of entering into any agreement or arrangement relating to the proposed Project/Tender.

- This Tender document, if includes certain statements, estimates, projections, designs, targets and forecasts with respect to the Project, such statements, estimates, projections, targets and forecasts, designs reflect various assumptions made by the management, officers and employees of APEPDCL, which assumptions (and the base information on which they are made) may or may not prove to be correct. No representation or warranty is given as to the reasonableness of forecasts or the assumptions on which they may be based and nothing in this document is, or should be relied on as a promise, representation or warranty.

- APEPDCL reserves the right to modify, amend or supplement or cancel this Tender document, without any prior notice or without assigning any reason.

Authorised Person:  Chief General Manager/Energy Conservation, Energy Audit& Solar Energy/

APEPDCL

Address:	                Eastern Power Distribution Company of  AP Ltd,

Corporate Office, P&T, Colony, Seethammadhara, Visakhapatnam-13

Visakhapatnam District Tel: 0891 -   2853776/764/771

E-mail:                     cgm_ec@apeasternpower.com, solar@apeasternpower.com

Place: 		    Visakhapatnam.

Date:		     02.12.2020

Information pertaining to Bid submission via e-Procurement platform

The	Bidder	shall	submit	response	to	the	tender	on	e-Procurement	platform	at https://tender.apeprocurement.gov.in by following the procedure given below.

The Bidder would be required to register on the e-procurement market place https://tender.apeprocurement.gov.in and submit their Bids online. Online submission of Bids is mandatory and Offline Bids shall not be entertained by the Tender Inviting Authority.

The Bidders shall submit their eligibility and qualification details, Bid Processing Fee and EMD (Prequalification), Technical Bid, Financial Bid etc., in the online standard formats displayed in e-Procurement web site. The Bidders shall upload the scanned copies of all the relevant certificates, documents etc., in support of their eligibility criteria/Technical Bid/Bid Processing Fee/EMD and other certificate/documents in the e-Procurement web site. The Bidder shall sign on the statements, documents, certificates, uploaded by him, owning responsibility for their correctness/authenticity. The Bidder shall attach all the required documents specific to the RfS after uploading the same during the Bid submission as per the RfS and Bid Documents.

- Registration with e-Procurement platform:

For registration and online Bid submission Bidders may contact HELP DESK of e procurement platform of Government of AP

https://tender.apeprocurement.gov.in.

- Digital Certificate authentication:

The Bidder shall authenticate the Bid with Digital Certificate for submitting the Bid electronically on e-Procurement platform. The Bids not authenticated by Digital Certificate of the Bidder will not be accepted.

For obtaining Digital Signature Certificate, you may please Contact: Andhra Pradesh Technology Services Limited,

Plot No. 302, 3rd Floor, Banukrishna Nilayam, Ashoka Nagar, Velanki Rammohan Rao street, Vijayawada

Mob: 9963029443/410

- Hard copies:

- Bidders shall submit hard copies of the Bid as specified in Clause 3.4 of this RfS, as per the timelines specified in Clause 3.2 of this RfS.

- All the Bidders shall invariably upload the scanned copies of DD/BG particulars in e- Procurement system and this will be one of the key requirements to consider the Bid responsive. Bid proposals received without the prescribed bid processing fees and EMD shall automatically be rejected

- Payment Of Transaction Fee:

It is mandatory for all the participant Bidders to electronically pay a Non-refundable Transaction fee to MD, APTS as per the relevant GoAP guidelines in regard to e-procurement fund to be administered by APTS limited, the service provider through "Payment Gateway Service on E-Procurement platform". The Electronic Payment Gateway accepts all Master and Visa Credit Cards issued by any bank and Direct Debit facility/Net Banking to facilitate the transaction. GST is applicable for Transaction on the transaction amount payable to MD APTS.

# Nodal Person for enquiries and clarifications

All correspondence, clarifications in respect of the Bid document and submission of the Bid shall be addressed to:

| Designation: | The Chief General Manager/ Energy Conservation, Energy Audit & Solar Energy/ APEPDCL |
| --- | --- |
| Address: | Eastern Power Distribution Company of AP Ltd, Corporate Office, P&T, Colony, Seethammadhara, Visakhapatnam Visakhapatnam District |
| Telephone: | 0891-2853776/764/771 |
| E-mail ids: | cgm_ec@apeasternpower.com, solar@apeasternpower.com |

- Tender Particulars

| Sl.No |  | Description |  |  |
| --- | --- | --- | --- | --- |
| 1 |  | Department Name | Eastern Power Distribution Company of AP Ltd (APEPDCL) |  |
| 2 |  | Office | The Chief General Manager/ Energy Conservation, Energy Audit & Solar Energy/APEPDCL |  |
| 3 |  | Tender Number | RfS No. CGM/EC,EA & Solar/GM/EC& Solar/APEPDCL – 01/2020-21 DATED : 02.12.2020 |  |
| 4 |  | Tender Subject | REQUEST FOR SELECTION OF EMPANELMENT FOR DESIGN, SUPPLY, INSTALLATION, TESTING & COMMISSIONING and Integrated Comprehensive Maintenance for 5 Years of Grid Connected Rooftop Solar Photovoltaic (PV) Power Units of capacity 1 KWp to 10 KWp for Residential sector in under Capex mode. |  |
| 5 |  | Tender Type | Open tender |  |
| 6 |  | Tender Category | Competitive bidding |  |
| 7 | Definitions and Interpretations |  | For the purpose of e-Procurement, the following definitions shall apply |
|  |  |  | - Tender Inviting Authority shall mean the same as Authorized Representative. - Tender Documents shall mean the same as the Bid document. - Commercial Bid” or “Price Bid” shall mean the same as the Financial Bid. - Bidders shall also upload a checklist of all documents enclosed under Technical Bid and Financial Bid and format as required under the Bid document. - EMD/Bid Security” shall mean the same as the EMD as per the provisions of this Bid document. - Bidder/Tenderer/Contractor shall mean one and the same. |
| 8 | Tender Validity Period |  | 180 Days from the Bid deadline date |
| 9 | Bid Security /EMD (INR) |  | As specified in the Bid document as per the prescribed Format, proposals would need to be accompanied by a Bid security in Indian Rupees for an amount of Rs.2.00 lakhs and valid for 60 days beyond the tender offer validity i.e 180 days +60 days. Firms claiming Exemptions for EMD shall submit valid Certificate/letter issued by Department of Micro, Small and Medium Enterprises (MSME) (or) are registered with the Central Purchase Organisation (or) the concerned Ministry or Department. |
|  |  |  | The bid security shall be kept valid 60 days beyond tender Validity Period of 180 days (i.e 180 days + 60 days) including any extensions in the Proposal Validity Period and would be required to be further extended if so required by APEPDCL. |
|  |  |  | Any extension of the validity of the Bid Security as requested by APEPDCL shall be provided by the agency a minimum of seven calendar days prior to the expiry of the validity of the Bid Security, being extended. |
| 10 | Bid Security/ EMD Payable to |  | As specified in Clause 3.2 of the RfS as per the prescribed format -3. It should be noted Bid Bond displayed on the NIT screen of the e-Procurement Website is not relevant to this procurement process. The actual EMD/Bid security to be submitted by the Bidder shall be as per Clause 3.2 of this RfS |
| 11 | Performance security |  | Successful bidders have to furnish DD/ BG as performance security as specified in the Bid document as per the prescribed Format, in Indian Rupees for an amount of Rs.5.00 lakhs and valid for 6 Years. |
| 12 | Transaction Fee & Bid processing fee |  | i)Transaction fee: All the participating bidders who submit the bids have to pay an amount of INR 10,000/- & applicable taxes as levied by the Govt. of India on transaction fee through online in favour of MD APTS, Vijayawada. The amount payable to the MD, APTS is non refundable. ii)Bid Processing Fee: The Tenderer shall pay an amount of INR 25,000/-plus GST @ 18% (or as in force) by way of Demand Draft in favour of Pay Officer, APEPDCL, Visakhapatnam payable at Visakhapatnam is non refundable. The scanned copy of the DD shall be uploaded and the original DD shall be furnished along with the tender document to APEPDCL. |
| 13 | Transaction Fee |  | Payable to the MD, APTS, Vijayawada, through online payment only. |
| 14 | Bid Processing Fee |  | by way of Demand Draft drawn in favour of The Pay Officer, APEPDCL, Visakhapatnam payable at Visakhapatnam. |
| 15 | Bid Document Download Start Date |  | 02.12.2020 from 17:00 Hours |
| 16 | Bid Document Download End Date |  | 06.01.2021 at 13:00 Hours |
| 17 | Pre-Bid Meeting |  | 16.12.2020 at 11.00Hrs at Corporate Office, APEPDCL, Visakhapatnam |
| 18 | Bid closing date |  | 06.01.2021 at 15:00 Hours for uploading technical Bid and Financial-Bid |
| 19 | Technical Bid Opening date |  | 06.01.2021, 16:00 Hours |
| 20 | Financial Bid Opening date |  | 16.01.2021, 16:00 Hours |
| 21 | Place of Tender Opening |  | O/o Chief General Manager/Energy Conservation, Energy Audit & Solar Energy/APEPDCL, Corporate office, APEPDCL. P&T Colony, Seethammadhara Visakhapatnam |
| 22 | Contact Officer |  | The Chief General Manager/ Energy Conservation, Energy Audit & Solar Energy/ APEPDCL |
| 23 | Address/E-mail id |  | The Chief General Manager Energy Conservation, Energy Audit & Solar Energy Eastern Power Distribution Company of AP Ltd, Corporate Office, P&T, Colony, Seethammadhara, Visakhapatnam-13 ,Visakhapatnam District. Email: solar@apeasternpower.com |
| 24 | Telephone Nos. |  | Telephone – 0891-2853776/764/771 |
| 25 | Procedure for Bid submission |  | The Bidder shall submit his response through Bid submission to the tender on e-Procurement platform at https://tender. apeprocurement.gov.in by following the procedure. The Bidder would be required to register on the e-procurement market place https://tender.apeprocurement.gov.in and submit their Bids online. Offline Bids shall not be entertained by the Tender Inviting Authority for the tenders published in e-Procurement platform. The Bidders shall submit their eligibility and qualification details, Technical Bid, Financial Bid etc., in the online standard formats displayed in e-Procurement web site. The Bidders shall upload the scanned copies of all the relevant certificates, documents etc., in support of their eligibility criteria / Technical Bid /EMD and other certificate/documents in the e-Procurement web site. EMD/ Bid security, to be submitted by the Bidder shall be as per Clause 3.2 of this RfS. The Bidder shall sign on the statements, documents, certificates, uploaded by him, owning responsibility for their correctness/authenticity. |
| 26 |  |  | Hard Copies: Bidders shall submit hard copies of EMD (Original DD/BG) and Bid Processing fee(Original DD) to the address mentioned in the respective clause of this Bid document before tender dead line. The Bidder shall upload the entire required documents specific to the Bid document in the e- tender platform duly signing each and every document. The bidder shall submit the hard copies of the Technical bid to the Authorised Representative either personally or through courier or post before the timelines as indicated in this tender document. Bidders shall also upload scanned copies of these documents ( DD towards processing fee and EMD/ Bid security) as part of the Qualification criteria of bid on the e-Procurement platform. All the Bidders shall invariably upload the scanned copies of DD/BG in e-procurement system and this will be one of the key requirements to consider the bid responsive. The Authorized Representative will not take any responsibility for any delay in receipt/non-receipt of original, Certificates/Documents from the successful Bidder before the stipulated time. On receipt of documents, the department shall ensure the genuinity of certificates/documents uploaded by the Bidder in e-Procurement system, in support of the qualification criteria before concluding the agreement. |
| 27 | Uploading |  | - Financial Bid shall be uploaded at the commercial stage available on the e-Procurement platform which has an encryption facility. - The Bidder shall AVOID zipping two versions of the same Financial Bid into a single folder. - In case the Authorized Representative finds multiple versions of the same Financial Bid in a single zip folder, such Bids are liable for rejection by the Authorized Representative. |

# INDEX

| Chapter No. | Topic | Page No |
| --- | --- | --- |
| 1 | Introduction and Background | 11-14 |
| 2 | Content of tender document | 15-16 |
| 3 | Preparation of tender | 17-18 |
| 4 | Submission of tender | 19-21 |
| 5 | Tender opening and evaluation | 22-23 |
| 6 | Finalisation of tenders | 24 |
| 7 | Terms of contract | 25-29 |
| 8 | Technical Specification | 30-44 |
| 9 | Technical Bid | 45-47 |
| 10 | Financial Bid | 48 |
| 11 | Formats & Check List | 49-61 |
| 12 | Annexures | 62- 77 |

CHAPTER-1

INTRODUCTION AND BACKGROUND

  - Introduction

MNRE (Ministry of New and Renewable Energy, Government of India) desires to implement grid connected rooftop solar PV projects on the roofs of Residential buildings and Residential Welfare Associations/Group Housing societies) as per  Phase II RTS guidelines issued with Subsidy for Residential category only and Incentives for Distribution Companies based on incremental capacity additions based on base capacity. This tender document is in accordance with MNRE Phase II guidelines vide notification 318/331/2017 dated 20.08.2019.

To implement the Rooftop Solar activities in respect of the aforesaid Projects, APEPDCL invites competitive Bids for EMPANELMENT FOR DESIGN,SUPPLY, INSTALLATION, TESTING & COMMISSIONING and Integrated Comprehensive Maintenance for 5 Years of Grid Connected Rooftop Solar Photovoltaic (PV) Power Units of capacity  1 KWp to 10 KWp for Residential sector in APEPDCL under CAPEX Mode. The period of contract is valid for a period 12 Months from the date of Empanelment.

This RfS shall be governed by terms of sanction received from MNRE vide F. No. 318/63/2019 Grid Connected Rooftop Dated 20.08.2019 for sanctioned capacity of  8 MW in Residential sector to APEPDCL and any amendments therein issued by MNRE till the date of award.

# 1.2 	Eligible Bidders

The Bidder shall provide sufficient documentary evidences to satisfy the following Conditions:

    - Has adequate financial stability and status to meet the financial obligations as per the financial Qualification Criteria of this tender

    - Has turnover and experience of Supply, Installation, Testing, Installation / commissioning and maintenance/after sale services in the field of Grid Connected Solar PV systems in the last 5 years as per the below criteria, and the details of the same must be submitted in the Proforma given in Technical- Bid section of tender document:

| Project Category | Financial Eligibility (Annual Turnover) | Technical Eligibility (Minimum Experience) |
| --- | --- | --- |
| 1KWp | Minimum cumulative turnover of Rs.1.00 crore during the last five financial years period (2015-2020) or net worth of Rs. 1 Crore as on 31.03.2020. | At least minimum 50KWp cumulative capacity Grid Connected Solar PV systems are installed in the last 5 Years. |
| Above 1 KWp upto 2KWp |  |  |
| Above 2 KWp upto 3KWp |  |  |
| Above 3 KWp upto 10KWp |  |  |

- Supporting Documents (Documentary evidence) against Eligibility Criteria mentioned above are work awarding/sanction copy/invoice , commissioning certificates/ Performance certificates to the extent of works done as per Technical eligibility

    - Supporting Documents (Documentary evidence) against Eligibility Criteria for commercial eligibility mentioned above are certificates pertaining to Turnover or networth from Chartered Accountant,

    - Has adequate field service setup to provide goods after sale services including necessary repair and maintenance in the jurisdiction of APEPDCL.

    - Has provided goods after sale services for the works done by him during past years.

    - Has Valid Test Certificates of the Solar PV Power Plant as specified and required in the Technical- Bid of this tender document.

    - Fulfills all requirements as per provisions under JNNSM, MNRE, GOI, GOAP. Only indigenously manufactured PV cells and modules will be used in project.

    - The bidder shall be required to have adequate post installation localized service facilities/ centers during the period of empanelment .

    - All the components including Power plant, software’s and other components mentioned above should be quoted as a single item. No partial quotes are accepted.

    - All the material used in Grid connected solar rooftop systems and allied equipment shall comply with the Technical specifications and standards of MNRE and APEPDCL being notified from time to time.

    - Bidder should have a valid PAN & GST registration certificate

    - The above stated requirements are compulsory to be fulfilled by the Bidder and APEPDCL may also ask for any additional information as may be deemed necessary in public interest.

1.3. 	ELIGIBLE CENTRAL FINANCIAL ASSISTANCE( CFA)

The MNRE will provide CFA for implementing of Solar Grid Connected and Small Solar  Power

Plants from 1KWp to 10KWp capacities in residential sector , as detailed below:

| Type of residential sector | CFA (as percentage of benchmark cost or cost discovered through competitive process whichever is lower ) |
| --- | --- |
| Residential sector (maximum up to 3 kW capacity ) | 40 % of benchmark cost** |
| Residential sector (above 3 kW capacity and up to 10 kW capacity)* | 40 % up to 3 KW Plus 20% for RTS system above 3 kW and up to 10 kW of benchmark cost** |
| Group Housing Societies/Residential Welfare Associations (GHS/RWA) etc. for common facilities up to 500 kWp (@ 10 kWp per house), with the upper limit being inclusive of individual rooftop plants already installed by individual residents in that GHS/RWA at the time of installation of RTS for common activity | 20% of benchmark cost** |

* The residential sector users may install RTS plant of even higher capacity as  provisioned by respective State electricity regulations; however, the CFA will be limited up to 10 kWp capacity of RTS plant.

** CFA shall be on benchmark cost of MNRE for the state/ UT or lowest of the costs discovered in the tenders for that state/ UT, whichever is lower

As per MNRE vide Notification Number 318/3/2020- Grid Connected Rooftop Solar dated 30th January 2020, “Para 5.1.4 of the operational guidelines for the Phase-II of RTS clearly indicate that the CFA will be calculated as a percentage of benchmark cost or cost discovered through competitive process whichever is lower. Therefore, it is hereby clarified that the rates discovered by the implementing agency through competitive bidding process or the benchmark cost, whichever is lower will be applicable for calculation of CFA under Phase II of grid connected rooftop solar programme for the RTS installed.”

It may be noted that the applicable subsidy amount shall be released directly to successful bidder(s) / developer(s)upon project commissioning, submission all requisite documentation as detailed in this RfS and receipt from MNRE. MNRE vide its notification No. 318/38/2018-Grid Connected Rooftop dated 21/7/2020 have decided the bench mark cost FY 2020-21 which is inclusive of total system cost and its installation, commissioning, transportation, insurance, capital cost of online monitoring, AMC/CMC for five years and applicable fees and taxes.

The CFA will be based on the scheme guidelines of Ministry of New and Renewable Energy (MNRE) which are amended from time to time.

- Solar modules shall comply with the Guidelines for enlistment under “Approved Models and Manufacturers of Solar Photovoltaic Modules (Requirements for Compulsory Registration) Order, 2019 ” issued by the MNRE vide F. No.283/54/2018-Grid Solar dated 06.09.2019.

- Manufacturers of solar panels/system integrators fulfilling technical and financial criteria are eligible for empanelment. The CFA for residential sector shall be permissible only if domestic manufactured Solar Panels (using domestic manufactured Solar cells) are used by the beneficiary/Vendor, they must furnish a undertaking (enclosed in Annexure A) on domestically manufactured content requirement (DCR)   as  communicated by MNRE

- Manufacturers of solar panels has adequate plant and manufacturing capacity available, to perform the works properly and expeditiously within the time frame specified in the tender document .

- Manufacturers of solar panels established quality assurance systems and organization designed to achieve high level of equipment reliability in manufacturing of the Solar Systems.

- Manufacturers of solar panels /system integrators must only use models of solar PV Cells & Modules domestically manufactured, they must furnish a undertaking (enclosed in Annexure A) on domestically manufactured content requirement (DCR)   as  communicated by MNRE.

- The system shall install as per minimum technical requirement /standards for SPV Systems/Plants given by MNRE in vogue and amended time to time. (Refer to MNRE website: www.mnre.gov.in)

- The installation shall be taken up through APEPDCL empanelled suppliers only as per the finalized rate contract rates.

- The eligibility of Central Financial Assistance (CFA) shall be as per the guidelines of Ministry of New and Renewable Energy (MNRE) in vogue and amended from time to time.

- The settlement of the project capacity installed would be done on the basis of prevailing MNRE benchmark cost or the tender cost, whichever is lower.

- The installation of the system shall be completed and commissioned on or before 90 days

- Proper metering arrangement may be incorporated so that the generation data from the proposed SPV power plants will be available.

- The release of CFA is subject to sanction and release of funds by MNRE and submission of all relevant documents.

- After completion and commissioning of the project the following documents shall be submitted in duplicate for considering release of CFA

- Copy of work

- Copy of invoice

- Joint inspection report in Original

- Project commissioning report in original

- Project Photographs (with beneficiary/organization)

- Synchronization letter

- Statement of Expenditure (SOE) duly certified by Charted Accountant in Original

- Electricity bill (After Commissioning)

- Authorisation letter for disbursement of subsidy to the system integrator.

- Beneficiary Photo & ID proof.

- Bank details of Vendor/System integrator.

# CHAPTER - 2

# TENDER DOCUMENT

  - 2.1 	Content of Tender Document

2.1.1  The tender procedure and contract terms are prescribed in the tender document. In addition to the invitation of tender, the tender document includes the various other documents as given in the table of particulars of tender.

2.1.2 The Bidder is expected to examine all instructions, terms and conditions,                     specifications, forms and formats etc as mentioned/ enclosed in the tender                    document. Failure to furnish all information required in the tender document or                   submission of a tender not substantially responsive to the tender document in  every respect will be at the Bidder’s risk and is likely to result in out-right  rejection of the tender.

# 2.2  INFORMATION REQUIRED WITH THE PROPOSAL

2.2.1 The tender must clearly indicate the name of the manufacturer, the types and model & make of each principal item of equipment proposed to be supplied.  The tender may also contain details of specifications and other comprehensive   descriptive materials in support of technical specifications.

    - The above information may be provided by the Bidder in the form of separate sheets, specifications, catalogues etc.

    - Any tender not containing sufficient descriptive material to describe the  proposed equipment may be treated as incomplete and hence may be rejected. Such descriptive materials and specifications submitted by the Bidder will be retained by APEPDCL. Any deviations from these will not be permitted during the execution of contract, without specific written permission of APEPDCL.

# 2.3 	CLARIFICATION OF TENDER DOCUMENT

2.3.1 Any prospective Bidder requiring any clarification on the tender document regarding various provisions / requirements/ preparation/ submission of the tender, may contact APEPDCL in writing by letter / email before 48 hours of closing time of the tender. Queries received later shall not be entertained.

2.3.2   Verbal clarifications and information shall not be entertained in anyway.

2.3.3	The Bidder(s) or their authorized representative(s) is /are invited to attend pre-bid meeting(s), which will take place on date(s) as specified in Bid information sheet, or any such other date as notified by APEPDCL

2.3.4	The purpose of the pre-bid meeting will be to clarify any issues regarding the RFS including in particular, issues raised in writing and submitted by the Bidders.

# 2.4  AMENDMENTS IN TENDER DOCUMENT

2.4.1	At any time prior to the due date for submission of the tender or even prior to the opening of the financial bid, APEPDCL may for any reason, whether at its own initiative or as a result of a request for clarification/ suggestion by a prospective Bidder, amend the tender document by issuing a notice.

2.4.2	The amendments will be notified as corrigendum on the e-procurement website at least 2 days before the proposed date of submission of the tender. APEPDCL will bear no responsibility or liability arising out of non-receipt of the information in time or otherwise.  If any amendment is required to be notified within 2 days of the proposed date of submission of the tender, the last date of submission shall be extended for a suitable period of time.

2.4.3	In case any amendment is notified after submission of the Bid prior to the opening of Techno- Commercial Bid due date /time shall be extended and it will be for the Bidders to submit fresh Bids/supplementary bids on date notified by the APEPDCL for the purpose.

# CHAPTER - 3

PREPARATION OF TENDER

  - 3.1 LANGUAGE OF TENDER AND MEASURE

The tender prepared by the Bidder along with all the related documents shall be in English. Unit measurements shall be metric in accordance with International System. All correspondence between the Bidder and APEPDCL shall also be in English.

# 3.2  EARNEST AND SECURITY MONEY

3.2.1	The Bidder shall furnish earnest money of Rs. 2,00,000/-  as mentioned in the “Particulars of Tender” in the shape of DD in favour of “Pay Officer, APEPDCL, Visakhapatnam” payable at Visakhapatnam.  Bank guarantee can also be submitted in place of DD towards EMD amount from any Nationalized   Bank in favour of the Chief General Manager, Energy Conservation, Energy Audit & Solar Energy/ APEPDCL, Visakhapatnam”, as a part of the tender. The bank guarantee should be valid for a period of 60 days beyond the validity of offer ( i.e 180 days + 60 days). Tenders without EMD shall be rejected by APEPDCL as being non-responsive. No interest shall be paid by APEPDCL on the amount of earnest money deposit deposition as well as deposition of Security Deposit. Firms claiming Exemptions for EMD shall submit valid Certificate/letter issued by Department of Micro, Small and Medium Enterprises (MSME) (or) are registered with the Central Purchase Organisation (or) the concerned Ministry or Department.

3.2.2  The earnest money may be forfeited:-

      - If a Bidder withdraws his tender during the specified period of validity of offer.

b)  If the successful Bidder fails to sign the contract agreement within stipulated period.

    - The earnest money of the successful Bidder shall be released at the time of signing of the agreement with APEPDCL.

    - The authority reserves the right of awarding the empanelment. The earnest money of such selected Bidder shall also be released or adjusted on the request of Bidder, on signing the agreement and submission security money by them. After receiving the consent, the earnest money of such Bidder shall be forfeited if they fail to sign the contract agreement within stipulated period.

    - The earnest money of all unsuccessful bidders shall be released soon after selection of selected bidder(s) against submission of their written intimation regarding empanelment and deposition of security deposit amount.

Performance security

    - The selected bidder shall have to deposit  Rs.5,00,000/- as Performance Security in the form of Demand Draft drawn in favour of “Pay Officer, APEPDCL, Visakhapatnam” payable at Visakhapatnam  OR Rs.5,00,000/- Bank Guarantee issued by any Nationalized  Bank in favour of The Chief General Manager, EC,EA& Solar APEPDCL, Visakhapatnam” valid for a period of 6 years(12 Months empanelment period + 5 years of integrated comprehensive maintenance).  No interest shall be paid by APEPDCL on the amount of security money deposit. The amount will be refunded after warranty period of last system installed.

# PERIOD OF VALIDITY OF TENDER

    - Validity of the offer should be 6 months from the proposed date of opening of the Technical bid. Tenders without this validity will be rejected.

    - In exceptional circumstances, APEPDCL may solicit the consent of the Bidder to an extension of the period of validity of offer. The request and the response there of shall be made in writing.

# FORMATS AND SIGNING OF TENDER

    - The tender must contain the name and places of business of the firm/person/persons participating in the tender and must be signed and sealed by the Bidder with his usual signature. The name and designation of all persons signing the tender document should be written below every signature. Tender by a partnership firm must be furnished with full name of all partners with a copy of partnership deed.

    - The original copy of the tender should be typed or written in indelible ink and must be signed with the legal name of the corporation/ company by the President/ Managing Director/ Secretary of the firm or a person duly authorized to bid. In case of authorized person the letter of authorization by written power-of-attorney should be enclosed with the technical bid of the tender. The person or persons signing the tender shall initial all pages of the tender document.

    - The tender shall contain no interlink actions, erasers or overwriting except as necessary to correct the errors made by the Bidder in the preparation of tender. The person or persons signing the tender shall also sign at all such corrections.

# PRICE AND CURRENCIES

The Bidder shall have to submit their rates in Indian Rupees only including all latest applicable taxes & duties of Govt. of Andhra Pradesh as well as Govt. of India. Moreover, APEPDCL will not be responsible for providing Road permits. It is to be obtained by the selected bidder only and necessary Entry Tax (as admissible) will have to be borne by the selected bidder if any. The rate should be quoted on the prescribed format for Financial Bid (Part II) attached to this tender document.

# CHAPTER – 4

SUBMISSION OF TENDER

4.1. The Bidder shall send EMD and processing fee in the form of DD/ Bank Guarantee, in original, on or before the Bid Deadline, to the address mentioned below:

The Chief General Manager/ Energy Conservation, Energy Audit & Solar Energy

Eastern Power Distribution Company of  AP Ltd,

Corporate Office, P&T, Colony, Seethammadhara, Visakhapatnam,

Visakhapatnam  Dt. Andhra Pradesh - 530 013.

  - The Bidder shall submit his response through Bid submission to the Bid document on e- Procurement platform at www.apeprocurement.gov.in by following the procedure given below.

  - The Bidder would be required to register on the e-procurement market place www.apeprocurement.gov.in or https://tender.apeprocurement.gov.in and submit their Bids online. Offline bids shall not be entertained by the Authorised Representative for this Bid document.

  - The Bidder shall upload Prequalification Bid, Technical Bid and the Financial Bid on the website. The information pertaining to Technical Bid and the Financial Bid shall be scanned and uploaded by the Bidder as per the formats specified.

  - The Bidders shall upload the scanned copies of all the relevant certificates, documents etc., in support of their Qualification Requirement and other certificate/documents in the www.apeprocurement.gov.in website. Each format has to be duly signed and stamped by the authorised signatory of the Bidder. The scanned copy of such signed and stamped format shall be uploaded by the Bidder on the website specified.

  - Strict adherence to the formats wherever specified, is required. Wherever, information has been sought in specified formats, the Bidder shall refrain from referring to brochures/pamphlets. Non-adherence to formats and/or submission of incomplete information may be a ground for declaring the Bid as non-responsive. Each format has to be duly signed and stamped by the authorized signatory of the Bidder. The scanned copy of such signed and stamped format shall be uploaded by the Bidder on the website specified.

  - The Bidder shall furnish documentary evidence in support of meeting Qualification Requirements set forth in the Bid document to the satisfaction of the Authorised Representative.

  - Important notes and instructions to Bidders

Wherever information has been sought in specified formats, the Bidders shall fill in the details as per the prescribed formats and shall refrain from any deviations and referring to any other document for providing any information required in the prescribed format.

The Bidders shall be evaluated based on the declarations and/or information and/or documents provided by them in relevant schedules of Bid document. The information and/or documents submitted along with the Bid may be verified before signing of agreement.

  - If the Bidder conceals any material information or makes a wrong statement or   misrepresents facts or makes a misleading statement in its Bid, in any manner whatsoever, Authorised Representative reserves the right to reject such Bid and/or cancel the Letter of Intent, if issued and the EMD provided up to that stage shall be en cashed. Bidder shall be solely responsible for disqualification based on their declaration in Bid.

  - If the event specified above is discovered after the Effective Date of the agreement,        consequences specified in agreement shall apply.

  - Bids submitted by the Bidder shall become the property of the Authorized Representative (APEPDCL) and the Authorized Representative shall have  no obligation to return the same to the Bidder. However, the EMDs submitted by unsuccessful Bidders shall be returned as specified.

  - All pages of the Bid submitted must be initialed by the person authorised by the board, on behalf of the Bidder.

  - No change or supplemental information to the Bid will be accepted after the Bid Deadline. The Authorised Representative may, at its sole discretion, ask for additional information/document and/or seek clarifications from a Bidder after the Bid Deadline, inter alia, for the purposes of removal of inconsistencies or infirmities in its Bid. However, no change in the substance of the Quoted rates shall be sought or permitted by the Authorised Representative. Delay in submission of additional information and/or documents sought by the Authorised Representative shall make the Bid liable for rejection.

  - All the information should be submitted in English language only.

  - Bidders shall mention the name of the contact person and complete address of the Bidder in the covering letter.

  - Bids that are incomplete, which do not substantially meet the requirements prescribed in this Bid document, will be liable for rejection by Authorised Representative. Bids not submitted in the specified formats will be liable for rejection by Authorised Representative. Non submission and/or submission of incomplete data/ information required under the provisions of Bid document shall not be construed as waiver on the part of Authorised Representative of the obligation of the Bidder to furnish the said data/ information unless the waiver is in writing.

  - The Qualified Bidder will be required to continue to maintain compliance with the Qualification Requirements specified in this Bid document throughout the bidding process and till the execution of the agreement. Where the Bidder is relying on affiliate/parent/ultimate parent for qualification, the Bidder shall continue to maintain this financial relationship till the execution of the agreement. Failure to comply with the aforesaid provisions shall make the Bid liable for rejection at any stage.

  - This Bid document includes statements, which reflect the various assumptions arrived at by the Authorised Representative in order to give a reflection of the current status in the Bid document. These assumptions may not be entirely upon by the Bidders in making their own assessments. This Bid document does not purport to contain all the information each Bidder may require and may not be appropriate for all persons. Each Bidder should conduct its own investigations and analysis and should check the accuracy, reliability and completeness of the information in this Bid document and obtain independent advice from appropriate sources.

  - Bidders shall quote price for the Solar Rooftop System/Project for each category that is quoted by the Bidder including Taxes and Duties.

  - Only Vishakhapatnam Courts shall have exclusive jurisdiction in all matters pertaining to this Bid document and decision of APEPDCL is final and binding in case of disputes if any.

  - APEPDCL may accept or reject any or all Bids without assigning any reason.

# CHAPTER-5

TENDER OPENING AND EVALUATION

  - 5.1 Bid evaluation methodology and selection

    - 1st Step – Prequalification (PQ)

    - 2st Step – Technical evaluation

    - 3rd Step – Financial Bid evaluation

# 1st  Step – Prequalification (PQ)

The Bidder shall submit the scanned copies of EMD in a separate folder in e- procurement platform. The Original of the same shall be submitted to the Authorised Representative before the Bid Deadline. Firms claiming Exemptions for EMD shall submit valid Certificate/letter issued by Department of Micro, Small and Medium Enterprises (MSME) (or) are registered with the Central Purchase Organisation (or) the concerned Ministry or Department.

The Bidder shall submit processing fee and original documents pertaining to EMD as specified. Bids not accompanied by EMD and Bid processing fee as per the terms of the tender document shall be summarily rejected and no further evaluation will be carried out in respect of such Bids/Bidders.

# 2nd  Step- Technical evaluation

Bids received after the Bid Deadline and Bids submitted without the EMD and Bid processing fee will be summarily rejected. Subject to above, all the formats, documents and/or information submitted by the Bidder as a part of the Technical Bid, except Financial Bid will be opened and evaluated at this stage.

The Bid submitted by the Bidder shall be scrutinized to establish technical eligibility as per Qualification Requirements of the tender.

Any of the following conditions shall cause the Bid to be “Non-responsive”:

(i)Non submission of EMD in acceptable form/amount along with the response to tender.

(ii)Non furnishing of copies of documents as specified in clause No1.2 for Technical eligibility.

(iii)Non furnishing of copies of documents as specified in clause No1.2 for commercial eligibility

(iv)Bids that are incomplete, i.e. not accompanied by any of the applicable formats, EMD,etc.;

(v)Bid not signed by authorized signatory and/or stamped in the manner indicated in this RFS;

(vi) Material inconsistencies in the information/ documents submitted by the Bidder, affecting

the Eligibility Criteria;

(vii)Information not submitted in the formats specified in this RFS;

(viii) Bid being conditional in nature;

(ix)Bid having Conflict of Interest;

(x) More than one Member of a Bidding Company using the credentials of the same Parent Company;

(xi) Bidder delaying in submission of additional information or clarifications sought by APEPDCL as applicable;

(xii) Bidder makes any misrepresentation.

(xiii)Any indication of the Quoted amounts in any part of Bid, other than in the financial Bid.

Subject to above, Authorised Representative will examine all the documents submitted by the Bidders and ascertain meeting of eligibility conditions prescribed in the tender. During the examination and evaluation of Bids, Authorised Representative may seek clarifications / additional documents / Rectification of errors / Discrepancies if any in the documents submitted etc. from the Bidders if required to satisfy themselves for meeting the eligibility conditions by the Bidders. Bidders shall be required to respond to any clarifications/additional documents sought by Authorised Representative within the timeline intimated by the Authorised Representative.

It shall be the responsibility of the Bidder to ensure that all the documents have been successfully uploaded on the e-procurement platform. No reminders in this case shall be sent. It will be the sole responsibility of the Bidders to remove all the discrepancies/infirmities and upload/furnish additional documents as requested by Authorised Representative, to the satisfaction of Authorised Representative. Authorised Representative shall not be responsible for rejection of any Bid on account of the above.

Bids meeting the Technical eligibility criteria and the Qualification Requirements specified in this tender shall be technically responsive and the corresponding Bidder shall be the Qualified Bidder.

# 3rd  Step – Financial Bid Opening and Bid evaluation

- Financial Bids of the Qualified Bidders shall be opened on the e-Procurement platform .

- Based on the Solar Rooftop system capacity specified in the Financial Bids, Bids received shall be segregated for each capacity i.e  1KWp, above 1 KWp upto 2 KWp, above 2 KWp upto 3 KWp, above 3 KWp upto 10 KWp.

- Ranking of Financial Bids shall be carried out by arranging them in ascending order of Bid Parameter for each of the category and the Bidder who quotes Lowest Price for the respective Solar rooftop capacity shall be designated as the L1 Successful Bidder.

- The Qualified Bidders participating shall be invited to match the Lowest Price in the ascending order of their rank as determined by MNRE .

“The selected bidders shall follow the quality control orders and standards for all components of RTS system and its installation procedure, if any, issued by MNRE from time to time.  All the bidders within the price bracket of (L1 + X% of L1) shall be empanelled. The digit “X” may be decided by the agency and should be clearly indicated while inviting Expression of Interest. The digit ”X” shall not be more than 25. Further, if total no. of empanelled agencies are found to be less than 5 in the acceptable band, then the DISCOM may also include those agencies who fall in L1+(X+5)% of L1, provided they agree to match L1.”

- If any Qualified Bidder doesn’t confirm to match the Lowest Price, such Qualified Bidder is removed from the Bid Process, without forfeiting the EMD, and the next Qualified Bidder in the ranking order is invited to match the Lowest Price.

- Upon signing of agreement with APEPDCL, the E.M.D of Successful Bidders and Bidders who did not accept the discovered price shall be returned to them within 15 days

# CHAPTER – 6

# FINALISATION OF TENDERS

6.1	Tenders will be finalized by the APEPDCL Tender evaluation committee, for the works along with technical bid evaluation for consideration and in accordance with the conditions stipulated in the tender document and in case of any discrepancy or non-adherence to the conditions, the same shall be communicated which will be binding both on the tender concluding authority and tenderer. In case of any ambiguity the decision taken by the APEPDCL on tenders shall be final.

  - The tenders if received with abnormally high percentage or within the permissible ceiling limits (bench mark cost) prescribed, but under collusion due to unethical practices adopted during the tendering process shall be rejected.

  - The Lowest Feasible Price discovered for each category of Projects shall be communicated to the Tenderer’s and the Tenderer’s are required to provide their acceptance for the same, within One Week from the date of notifying as per MNRE Guidelines.

  - The Tenderer who has quoted the Lowest Feasible Price shall have to mandatorily accept the Price or else forfeit their E.M.D. Other Tenderer’s who accept to abide by the Lowest Feasible Price shall be considered as Successful Tenderer’s, and the E.M.D of Other Tenderer’s who do not wish to accept the discovered price shall be returned.

  - The Successful Tenderer has to sign an agreement with in a period of 15 days from the date of receipt of communication of acceptance of his tender. On failure to do so, his tender will be cancelled, duly forfeiting the E.M.D paid by him without issuing any further notice.

  - Upon signing of agreement with APEPDCL the E.M.D of Successful Tenderer’s and Tenderers who did not accept the discovered price shall be returned to them within 15 days.

# CHAPTER -7

TERMS OF CONTRACT

7.1 EVALUATION CRITERION

The whole work shall be on Turnkey basis. The empanelment of tenderer shall be finalized on the basis of cost of Solar Power Plant system including DESIGN,SUPPLY, INSTALLATION, TESTING & COMMISSIONING and Integrated Comprehensive Maintenance for 5 Years of Grid Connected Rooftop Solar Photovoltaic (PV) Power Units of capacity 1 KWp to 10 KWp for Residential sector in APEPDCL  as offered by the tenderer in his Financial Bid.

# 7.2 NOTIFICATION OF EMPANELMENT

Prior to the expiry of validity period of offer, APEPDCL will notify the successful Bidders by registered Letter/Email that he is empanelled as one of the Bidders accepted to install the solar rooftop power plants under the AP state solar rooftop policy amended from time to time.

# 7.3 EMPANELMENT

Before empanelment as approved supplier, an agreement shall be signed between APEPDCL and the Bidders. The denial of the lowest bidder to undertake the whole work shall be treated as breach of contract and APEPDCL may forfeit EMD/ Security amount submitted by him.

7.4  RIGHT TO ACCEPT/REJECT ANY OR ALL TENDERS.

APEPDCL reserves all the right to reject any or all the tenders, accept any tender in total or in part.

# 7.5  EXPENSES OF AGREEMENT

The respective suppliers shall pay all the expenses of stamp duties and other requirements for signing the agreement with APEPDCL.

# 7.6  EXECUTION OF AGREEMENT OF EMPANELMENT

    - The Successful Bidder shall execute an agreement of empanelment in the INR 200 non-judicial stamp paper of Andhra Pradesh Jurisdiction only in the name of the Bidders, within 15 days from the date of Letter of Intimation about qualification by APEPDCL.

    - The Successful Bidder shall not assign or make over the empanelment, the benefit or burden thereof to any other person or persons or body corporate for the execution of the contract or any part thereof without the prior written consent of APEPDCL. APEPDCL reserves its right to cancel the empanelment either in part or full, if this condition is violated.

    - In case of the successful bidder fails to execute necessary agreements as prescribed, within the stipulated period, then his EMD shall be forfeited and his tender held as non-responsive.

# ISSUE OF LETTER OF EMPANELMENT

After execution of the Agreement and payment of Performance Security Deposit, the name of successful bidder(s) with price will be displayed in website of APEPDCL and a letter of empanelment will be sent to the qualified Bidders.

7.9  INSTALLATION & COMPLETION SCHEDULE

The entire work involving Supply, Installation and Commissioning of each Grid connected Solar Rooftop power plants shall be completed within 90 days for all capacities from the date of issue of work order by the end user or beneficiary

  - SCOPE OF WORK

- Scope of work covers Design, Supply, Installation, Commissioning, Synchronisation, including

Maintenance and Operation for a period of five years & Insurance of Grid Connected SPV Rooftop Plant of capacity 1 KWp to 10 KWp for Residential sector in APEPDCL. as per the technical specifications and standards notified by MNRE/APEPDCL/CEA/CEIG.

- The cost is inclusive of all taxes, duties, packing, forwarding and transportation costs upto the site.

- Wiring up to Distribution Board from the SPV Rooftop system will be in the scope of the successful bidder(s). The maximum cable length of 50 m for every solar power plant installed shall be in the scope of the bidder and supply of excess cable length if required shall be in the scope of purchaser.

- Mounting Structure within the scope of this tender is for flat RCC roofs. If the roof is not flat and requires additional mounting structure then the cost will have to be separately borne by the applicant.

- Performance testing of the complete system.

- The empanelled installer shall undertake to supply spares free of cost for the maintenance of the offered items during the warranty period.

- A leaflet containing the details of the service centres shall be provided to each purchaser as well as to APEPDCL.

- If the operation or use of the system proves to be unsatisfactory during the warranty period, the installer shall replace the faulty ones or carry out necessary repairs as per the warranty terms and conditions.

- The beneficiary will have to install RTS system through any of these empanelled vendors at net of CFA amount i.e. making payment to the vendors after deducting the eligible CFA amount. The vendor will claim the CFA from the APEPDCL. The CFA for residential sector as stated above shall be permissible only if domestic manufactured Solar Panels (using domestic manufactured Solar cells) are used by the beneficiary. The eligible MNRE subsidy will be released depending on the availability of budget released by MNRE, based on MNRE Policies and guidelines.

- The procedure for availing subsidy and for submission of proposals shall be as per details uploaded in the web-site: www.apeasternpower.com

- The empanelled installer will collect firm work order from the beneficiary. A copy of Work Order, Invoice, Commissioning report Statement of Expenditure, Joint Inspection Report, Metering Work Completion as applicable & Synchronization reports, vacant area photographs, installed system photographs, beneficiary photo, Aadhar card, mobile no & Electricity bill (before and after installation) and bill of material, handing over certificate and the panel serial nos. has to be submitted to APEPDCL for processing CFA. The eligible MNRE subsidy will be released depending on the availability of budget released by MNRE, based on MNRE Policies and guidelines, the DISCOMs shall disburse the CFA to vendors within two weeks.

The subsidy as calculated will be released on submission of following documents- (i) Joint Commissioning Report (JCR) (ii) Copy of Insurance Policies (iii) Claim Letter (iv) Guarantee certificate on Letter Head of the Vendor, (v) Self declaration for domestic content requirement (DCR) (vi) Performance security (of DISCOM Part) for O&M Period. The bidder shall provide the above document and any other document as may be asked by DISCOM / MNRE for release of subsidy.

The Empanelled Installer shall do necessary coordination with concerned agencies like APEPDCL and CEIG, as applicable, for procuring necessary approvals on behalf of the Purchasers. However the cost of approvals and meter, CT/PT etc shall be borne by the  purchaser only.

- All successful bidder(s) have to get there work directly from prosumers. The successful bidder(s) will give useful training to the prosumers.

Broad Scope of Work for Consumer and successful bidders are:

Scope of Consumer:

- Cleaning and clearing the roof-top of any unwanted things and making it suitable for erection of the solar roof top power plant.

- Drinking water services in the power plant complex and suitable water supply for periodic cleaning of solar PHOTO VOLTAIC modules.

Scope of the Successful Bidder shall also include:

- Site Survey, Measurement of solar isolation and other relevant parameters required for design of each system.

- Complete Design, engineering, preparation and submission of drawings Equipment and material specification preparation.

- Procurement and expediting of all supplies and Delivery of equipment and material to each job site.

- Pre-commissioning & Commissioning of all supplied Equipment and Test running of Grid Connect Rooftop Solar Photovoltaic system.

- Any other items not specifically mentioned in the specification, but which are required for erection, testing and commissioning and satisfactory operation of the solar power plant are deemed to be included in the scope of the specification unless specifically excluded on turnkey basis.

- Provision of Safety items like hand gloves, shock treatment charts, rubber mats, danger/caution boards.

- Supply of all commissioning spares and Supply of special tools and tackles. Project management including project administration, project coordination, scheduling, progress reporting to employer and adhering to safety practices during erection, commissioning and subsequent operation and maintenance of the system including fire prevention.

- Operation and Maintenance Manual:

- An Operation, Instruction and Maintenance Manual in English/Hindi languages should be provided with the Solar PHOTO VOLTAIC projects. The following minimum details must be provided in the Manual:

- Basic principles of Photovoltaic.

- A small write-up (with a block diagram) on the Solar PHOTO VOLTAIC project - its components, PHOTO VOLTAIC module, inverter, junction boxes and expected performance shall be provided.

- Type, Model number, Voltage & capacity of inverter, used in the system.

- The make, model number, country of origin and technical characteristics of the entire component are required to be provided.

- Clear instructions on regular maintenance and troubleshooting of the Solar PHOTO VOLTAIC Projects.

- DO's and DONT's.

- Name, address and Mobile No. of the contact person for repair and maintenance in  case of non-functionality of the RTS Projects.

# 7.11. INSPECTION BY APEPDCL

All the SPV Rooftop systems installed will be inspected by the representative of APEPDCL within 10 days of receipt of Installation & Commissioning Certificate. The eligible amount will be released only for the systems installed in compliance to the technical specification of MNRE /CEIG/APEPDCL.  During the Inspection, if the system installed is found faulty (or) not in compliance to the technical specification, the cost for re-inspection by APEPDCL after rectification/replacement shall be borne by the Tenderer.

# 7.12  SERVICE CENTRES

Empanelled Installer shall have 2 service centers in the jurisdiction of APEPDCL. In case if it is not economically viable for an individual Empanelled Installer, then Group of three (3) or less Empanelled Installers can establish service center jointly . The service center details shall be made available at the time of entering into agreement with APEPDCL and the same will be displayed  on the website of APEPDCL. These service centres have to provide services to the RTS owners within the timelines decided by the DISCOMs, free of cost for first five years (Warranty period) of commissioning the RTS.

The Installer shall visit the site at least once in a quarter, to attend routine maintenance, during the 5 years warranty period. However, in case of malfunctioning of the system, the bidder shall attend for rectification of defects within 5 working days from the date of lodging complaint. if the empanelled vendors still find violating the provisions of the integrity pact provided in the bid during the installation he execution of plant and/or In case the systems are not as per standards, non-functional on account of poor quality of installation, or non-compliance of CMC, then empanelment of such vendors are liable to be cancelled. In addition to this, APEPDCL/MNRE reserves the right to award punishment to such empanelled vendor, which includes forfeiture of their submitted Performance Security and/or blacklisting. Such Vendor will be barred from participating in the tenders for a period of 1 year.

# 7.13  WARRANTY

- (a)   The SPV panel shall carry a warranty of minimum 25 years.

- The SPV panel must be warranted for their output peak watt capacity which shall not be less than 90% at the end of 10 years and 80% at the end of 25 years.

- The PCU/Solar Grid tie Inverter shall carry a warranty of minimum 5 years.

- The complete SPV rooftop systems installed and commissioned shall be under a warranty against any manufacturing or usage defect for a minimum period of 5 years from the date of Commissioning. The mechanical structures, electrical works including power conditioners/inverters/maximum power point tracker units/ distribution boards/digital meters/ switchgear etc. and overall workmanship of the SPV rooftop systems must be warranted against any manufacturing/ design/ installation defects for a minimum period of 5 years.

- The warranty will be against breakages, malfunctions, non-fulfillment of guaranteed performance and breakdowns due to manufacturing defects or defects that may arise due to improper operation of electrical /electronic components of the system but do not include physical damages by the end users/beneficiary.

- The above warranty shall take effect from the date on which the system is taken over by the purchaser after commissioning Synchronizing.

- The successful bidder shall be liable to make good the loss by replacing the defective product during the warranty period for the entire system free of cost.

- The warranty will cover all the materials and goods involved in the installation and commissioning of SPV rooftop systems by the successful Bidder.

- Non-performing/Under-performing PV Panels will be replaced free of cost in the warranty period. Non-compliance of the service standards by the vendor will make it ineligible for future work orders.

# 7.14  VALIDITY OF EMPANELMENT

The validity of Empanelment and the price accepted shall be 12 months.

# 7.15  APEPDCL RESERVES THE RIGHT TO;

Negotiate with the Bidders for further reduction of prices.

# 7.16  BANNING OF BUSINESS DEAL:

The bidder/consortium will be banned from business with APEPDCL if any of the particulars produced by the bidder such as Auditor Certificate, Annual account, GST Clearance Certificate, Test certificate, etc. are found to be incorrect, or if there is breach of any of the conditions in the contract.

7.17 INSURANCE

7.17.1 The Vendor shall be responsible and take an Insurance Policy for transit-cum- storage-cum-erection for all the materials to cover all risks and liabilities for supply and storage of materials at site, erection, testing and commissioning.

7.17.2 Before commencement of work, the Vendor shall also take insurance for Third Party Liability covering loss of human life, engineers and workmen and also covering the risks of damage to the third party/ material/ equipment/ properties during execution of the Contract. The Vendor will ensure that all its employees and representatives are covered by suitable insurance against any damage, loss, injury or death arising out of the execution of the work or in carrying out the Contract. Liquidation, Death, Bankruptcy etc., shall be the responsibility of bidder.

7.17.3 The vendor shall also take appropriate insurance during O&M period.

7.17.4 The Insurance covers as mentioned in clause no. 7.17.1, 7.17.2 & 7.17.3 are mandatory and in case of any violation of not taking Insurance Cover may result in imposition of Penalty. Penalty shall be deducted from the Vendors claim for subsidy as under and the subsidy, in such cases shall be released only on submission of Indemnity Bond @  Rs.5,000/per site - for plants having capacity >1-10kWp.

The provision of penalty for not taking insurance is one time only, on repetition of the same, the sanctioned of the particular site will be cancelled

CHAPTER -8

TECHNICAL SPECIFICATION

## 8.1  INTRODUCTION

In grid-connected Solar Photo-Voltaic (SPV) systems, solar energy is fed into the building loads that are connected to the public electricity grid. For buildings with grid-connected solar PV systems, the service connection meter & billing shall be as directed by APEPDCL/APERC/GOAP and  amended from time to time.

### 8.2 QUALITY AND WORKMANSHIP

Solar PV modules are designed to last 25 years or more. It is therefore essential that all system components and parts, including the mounting structures, cables, junction boxes, distribution boxes and other parts also have a life cycle of at least 25 years. Therefore all works shall be undertaken with the highest levels of quality and workmanship. During inspection APEPDCL and its representatives will pay special attention to neatness of work execution and conformity with quality and safety norms. Non compliant works will have to be redone at the cost of the Installer.

### 8.3  DEFINITION

A Grid Tied Solar Rooftop Photo Voltaic (SPV) power plant consists of SPV array,  Module Mounting Structure, Power Conditioning  Unit  (PCU)  consisting of  Maximum  Power  Point Tracker (MPPT), Inverter, and  Controls  & Protections, interconnect cables and switches. PV  Array is mounted on a suitable structure. Grid tied SPV system is without battery and should be designed with necessary features to supplement the grid power during day time. Components and parts used in the SPV power plants including the PV modules, metallic structures, cables, junction box, switches, PCUs etc., should conform to the BIS or IEC or international specifications,  wherever such specifications are available and applicable.

Solar PV system shall consist of following equipments/components.

- Solar PV modules consisting of required number of Crystalline PV modules

- Grid interactive Power Conditioning Unit with Remote Monitoring System

- Mounting structures

- Junction Boxes.

- Earthing and lightening protections.

- IR/UV protected PVC Cables, pipes and accessories

### SOLAR PHOTOVOLTAIC MODULES:

8.4.1 Only domestic manufactured PV modules (using domestic manufactured solar cells) with RFID and the manufacturer should provide the following minimum information laminated inside the module:

      - Made in India (to be subscribed in words)

      - Company name / logo

      - Module number (it should indicate the voltage and rated wattage of the module)

      - Serial number

      - Year of make

    - The PV modules used must qualify to the  latest  edition  of  IEC PV module qualification test or equivalent BIS standards Crystalline Silicon Solar Cell Modules IEC 61215/IS14286. In addition, the modules must conform to IEC 61730 Part-1- requirements for construction & Part 2 – requirements for testing, for safety qualification or equivalent IS.

- For the PV modules to be used in a highly corrosive atmosphere throughout their lifetime, they must qualify Salt Mist Corrosion Testing as per IEC 61701/IS 61701

- The total solar PV array capacity should not be less than allocated capacity (KWp) and should comprise of solar crystalline modules of minimum 250Wp and above wattage. Module capacity less than minimum 250 watts should not be accepted.

- Protective devices against surges at the PV module shall be provided. Low voltage drop bypass diodes shall be provided.

- PV modules must be tested and approved by one of the MNRE/NABL/IEC authorized test centers. The module frame shall be made of corrosion resistant materials, preferably having anodized aluminum. In case of Mild Steel or High Tensile steel for module mounting structure, minimum coating of zinc for galvanization shall be 610 g/sq.m.as per relevant Indian Standard.

- The bidder shall carefully design & accommodate requisite numbers of the modules to achieve the rated power in his bid. APEPDCL shall allow only minor changes at the time of execution.

- Other general requirement for the PV modules and subsystems shall be the Following:

- The rated output power of any supplied module shall have tolerance of +/- 3%.

- The peak-power point voltage and the peak-power point current of any supplied module and/or any module string (series connected modules) shall not vary by more than 2 (two) per cent from the respective arithmetic means for all modules and/or for all module strings, as the case may be.

- The module shall be provided with a junction box with either provision of external screw terminal connection or sealed type and with arrangement for provision of by-pass diode. The box shall have hinged, weather proof lid with captive screws and cable gland entry points or may be of sealed type and IP-65 rated.

8.4.3	I - V curves at Standard Test Condition (STC)should be provided by bidder. Modules deployed RF identification tag. The following information to be mentioned in the RFID used on each modules (This has to be inside the laminate, but must be able to withstand harsh environmental conditions).

- Name of the manufacturer of the PV module

- Name of the manufacturer of Solar Cells.

- Month & year of the manufacture (separate for solar cells and modules)

- Country of origin (separately for solar cells and module)

- I-V curve for the module Wattage, Im, Vm and FF for the module

- Unique Serial No and Model No of the module

- Date and year of obtaining IEC PV module qualification certificate.

- Name of the test lab issuing IEC certificate.

- Other relevant information on traceability of solar  cells  and  module  as  per ISO  9001 and ISO 14001

8.4.4  Warranties:

- Material Warranty:

  - Material Warranty is defined as: The manufacturer should warrant the Solar Module(s)    to be free from the defects and/or failures specified below for a period not less than five (05) years from the date of sale to the original customer ("Customer").

  - Defects and/or failures due to manufacturing

  - Defects and/or failures due to quality of materials

- Non conformity to specifications due to faulty manufacturing and/or inspection processes. If the Solar Module(s) fails to conform to this warranty, the manufacturer will repair or replace the solar module(s), at the Owners sole option.

Performance Warranty:

  - The predicted electrical degradation of power generated not exceeding 20% of the minimum rated power over the 25 year period and not more than 10% after ten years period of the full rated original output.

8.5 ARRAY STRUCTURE

    - Hot dip galvanized MS mounting structures may be used for mounting the modules/ panels/arrays. Each structure should have angle of inclination as per   the   site   conditions to take maximum insulation. However to accommodate more capacity the angle inclination may be reduced until the plant meets the specified performance ratio requirements. Minimum thickness of galvanization should be at least 120 microns.

    - The Mounting structure shall be so designed to withstand the speed for the wind zone of  the location where a PV system is proposed to be installed (like wind speed of 200 kM/ hour). It may be ensured that the design has been certified by a recognized Lab/ Institution  in this regard and submit wind loading calculation sheet to APEPDCL/User. Suitable fastening arrangement such as grouting and calming should be provided to secure the installation against the specific wind speed.

    - The mounting structure steel shall be as per latest IS 2062: 1992 and galvanization of the mounting structure shall be in compliance of latest IS 4759.

    - Structural material shall be corrosion resistant and electrolytically compatible with the materials used in the module frame, its fasteners, nuts and bolts. Aluminum structures also can be used which can withstand the wind speed of respective wind zone. Necessary protection towards rusting need to be provided either by coating or anodization.

    - The fasteners used should be made up of stainless steel with strictly provision to seal with

adhesive/sealant / glue for avoiding from rust and corrosion and prevents loosening from

shock and vibration..  The  structures  shall  be  designed to allow easy replacement of any module. The array structure shall  be  so designed that it will occupy minimum space without sacrificing the output from the SPV panels

    - Regarding civil structures the  bidder  need  to  take  care  of  the  load  baring capacity  of the roof and need arrange suitable structures based on the quality of roof.

    - The total load of  the  structure  (when  installed  with  PV  modules)  on  the terrace should be less than 60 kg/m2.

    - The minimum clearance of the structure from the roof level should be 300 mm. Provision for safe and secure access to roof top as well as arrangement of proper cleaning of entire arrays i.e walkways, ladders and platforms on elevated/ above ground structures shall be in the scope of vendor.

  - JUNCTION BOXES (JBs)

- The junction boxes are to be provided in the PV array  for  termination  of  connecting  cables. The J. Boxes (JBs) shall be made of GRP/FRP/Powder Coated Aluminum /cast aluminum alloy with full dust, water & vermin proof arrangement. All wires/cables must be terminated through cable lugs. The JBs shall be such that input & output termination can be made through suitable cable glands.

- Copper bus bars/terminal blocks housed in the junction box with suitable  termination  threads Conforming to IP65 and IEC  62208  Hinged door with  EPDM rubber  gasket to prevent water entry. Single/ double compression cable glands. Provision of earthings. It should be placed at 5 feet height or above for ease of accessibility.

- Each Junction Box shall have High quality Suitable capacity Metal Oxide Varistors (MOVs) /SPDs,   suitable   Reverse   Blocking  Diodes.   The Junction  Boxes shall have suitable arrangement monitoring and disconnection for each of the groups.

- Suitable markings shall be provided on the bus bar for easy identification and the cable ferrules must be fitted at the cable termination points for identification.

- All fuses shall have DIN rail mountable fuse holders and shall be housed in thermoplastic IP 65 enclosures with transparent covers

### DC DISTRIBUTION BOARD:

- DC Distribution panel to receive the DC output from the array field.

- DC DPBs shall have sheet from enclosure of dust & vermin proof conform to IP 65 protection. The bus bars are made of copper of desired size. Suitable capacity MCBs/MCCB shall be provided for controlling the DC power output to the PCU along with necessary surge arrestors.

8.8       AC DISTRIBUTION PANEL BOARD:

- AC Distribution Panel Board (DPB) shall control the AC power from PCU/ inverter, and should have necessary surge arrestors. Interconnection from ACDB to mains at LT Bus bar while in grid tied mode.

- All switches and the circuit breakers,  connectors  should  conform  to  IEC 60947, part I, II  and III/ IS60947 part I, II and III.

- The changeover switches, cabling work should be undertaken by the bidder as part of the project.

- All the Panels shall be metal clad, totally enclosed, rigid, floor mounted, air - insulated, cubical type suitable for operation on three phase / single phase, 415 or 230 volts, 50 Hz.

- The panels shall be designed for minimum expected ambient temperature of 45 degree Celsius, 80 percent humidity and dusty weather.

- All indoor panels will have protection of IP54 or better. All outdoor panels will have protection of IP65 or better.

- Should conform to Indian Electricity Act and rules (till last amendment).

- All the 415 AC or 230 volts devices / equipment like bus support insulators, circuit breakers, SPDs, VTs etc., mounted inside the switchgear shall be suitable for continuous operation  and satisfactory performance under the following supply conditions

| Variation in supply voltage | +/- 10 % |
| --- | --- |
| Variation in supply frequency | +/- 3 Hz |

### 8.9  PCU/ARRAY SIZE RATIO:

- The combined wattage of all inverters should not  be  less  than  rated capacity of power  plant under STC.

- Maximum power point tracker shall be integrated in the PCU/inverter to maximize energy drawn from the array.

### 8.10 PCU/ Inverter:

As SPV array produce direct current electricity, it is necessary to convert this direct current into alternating current and adjust the voltage levels to match the grid voltage. Conversion shall be achieved using an electronic Inverter and the associated control and protection devices. All these components of the system are termed the “Power Conditioning Unit (PCU)”. In addition, the PCU shall also house MPPT (Maximum Power Point Tracker), an interface between Solar PV array & the Inverter, to the power conditioning unit/inverter should also be DG set  interactive. If necessary, Inverter output should be compatible with the grid frequency. Typical technical features of the inverter shall be as follows:

- Switching devices	: IGBT/MOSFET

- Control	: Microprocessor /DSP

- Nominal AC  output  voltage and frequency	: 415V, 3 Phase, 50 Hz (In case single phase inverters are offered, suitable arrangement for balancing the phases must be made.)

- Output frequency	: 50 Hz

- Grid Frequency Synchronization range	: + 3 Hz or more

- Ambient temperature considered	: -20o C to 50o C

- Humidity	: 95 % Non-condensing

- Protection of Enclosure	: IP-54(Minimum) for indoor.

: IP-65(Minimum) for outdoor.\

- Grid Frequency Tolerance range	: + 3 or more

- Grid Voltage tolerance	: - 20% & + 15 %

- No-load losses	: Less than 1% of rated power

- Inverter efficiency(minimum)	: >93% ( In case of 10kW or above )

- Inverter efficiency (minimum )	: > 90% (In case of less than 10 kW)

- THD	: < 3%

            - (as per IEEE 519 as amended from time to time)

- PF	: > 0.9

    - Three phase PCU/ inverter shall be used with each power plant  system (3kW  and/or  above) but In case of less than 3 KW single phase inverter can be used.

    - PCU/inverter shall be capable of complete automatic operation including wake-up, synchronization & shutdown.

    - The output of power factor of PCU inverter is suitable for all voltage ranges or sink of reactive power, inverter should have internal protection arrangement against any sustainable fault in feeder line and against the lightning on feeder.

    - Built-in meter and data logger to monitor plant performance through external computer shall be provided.

    - The power conditioning units / inverters should comply with applicable IEC/ equivalent BIS standard for efficiency  measurements  and  environmental tests  as  per  standard  codes IEC 61683/IS 61683 and IEC 60068-2(1,2,14,30) /Equivalent BIS Std.

    - The charge controller (if any) / MPPT units environmental testing should qualify IEC 60068-2(1, 2, 14, 30)/Equivalent BIS std. The junction boxes/ enclosures should be IP 65(for outdoor)/ IP 54 (indoor) and as per IEC 529 specifications.

    - The PCU/ inverters should be tested from the MNRE approved test centres / NABL /BIS /IEC accredited testing- calibration laboratories. In case of imported power conditioning units,  these should be approved by international test houses.

    - Anti-islanding (Protection against Islanding of grid): The PCU shall have anti islanding protection in conformity to IEEE 1547/UL 1741/ IEC 62116 or equivalent BIS standard.

    - Channel Partner shall be responsible for galvanic isolation of solar roof top power plant (>100kW) with electrical grid or LT panel.

    - In PCU/Inverter, there shall be a direct current isolation provided at the output by means of a suitable isolating transformer. If Isolation Transformer is not incorporated with PCU/Inverter, there shall be a separate Isolation Transformer of suitable rating provided at the output side of PCU/PCU units for capacity more than 100 kW.

    - The PCU/ inverter generated harmonics, flicker, DC injection limits, Voltage Range, Frequency Range and Anti-Islanding measures at the point of connection to the utility services should follow the latest CEA(Technical Standards for Connectivity Distribution Generation Resources) Guidelines.

### 8.11  INTEGRATION OF PV POWER WITH GRID:

The output power from SPV would be fed to the inverters which converts DC produced by SPV array to AC and feeds it into the main electricity grid after synchronization. In case of  grid failure, or low or high  voltage,  solar  PV system shall be out of synchronization and  shall be disconnected from the grid. Once the DG set comes into service PV system shall again be synchronized with DG supply and load requirement would be met to the extent of availability of power. 4 pole isolation of inverter output with respect to the grid/ DG power connection need to be provided.

### 8.12 DATA ACQUISITION SYSTEM / PLANT MONITORING

- Data Acquisition System shall be provided for each of the solar PV plant.

- Data Logging  Provision  for  plant  control  and  monitoring,  time  and  date  stamped system data logs for analysis with the high quality, suitable PC. Metering and Instrumentation for display of systems parameters and status indication to be provided.

- Solar Irradiance: An integrating Pyranometer / Solar  cell based irradiation sensor (along  with calibration certificate) provided, with the sensor mounted in the plane of the array. Readout integrated with data logging system.

- Temperature: Temperature probes for recording the Solar panel temperature and/or ambient temperature to be provided  complete  with  readouts integrated with the data logging  system

- The following parameters are accessible via the operating interface display in real time separately for solar power plant:

- AC Voltage.

- AC Output current.

- Output Power

- Power factor.

- DC Input Voltage.

- DC Input Current.

- Time Active.

- Time disabled.

- Time Idle.

- Power produced

- Protective function limits (Viz-AC Over voltage, AC Under voltage, Over frequency, Under frequency ground fault, PV starting voltage, PV stopping voltage.

- All  major  parameters  available  on  the  digital  bus  and  logging  facility  for  energy auditing through the internal microprocessor and read on the digital front panel at any time) and logging facility (the current values, previous values for up to a month and the average values) should be made available for energy auditing through the internal microprocessor and should be read on the digital front panel.

- PV array energy production: Digital Energy Meters to log the actual value of AC/ DC voltage, Current & Energy generated by the PV system provided. Energy meter along with CT/PT should be of 0.5 accuracy class.

- Computerized DC String/Array monitoring and AC output monitoring shall be provided as part of the inverter and/or string/array combiner box or separately.

- String and array DC Voltage, Current and Power, Inverter AC output voltage and current (All

3 phases and lines), AC power (Active, Reactive and Apparent), Power Factor and AC energy (All 3 phases and cumulative) and frequency shall be monitored.

- Computerized AC energy monitoring shall be in addition to the digital AC energy meter.

- The  data shall be  recorded in a common work sheet chronologically date wise. The data   file shall be MS Excel compatible. The data shall be represented in both tabular and graphical form.

- All instantaneous data shall be shown on the computer screen.

- S o f t w a r e shall be provided for USB download and  analysis  of  DC  and  AC parametric data for individual plant.

- Provision for Internet monitoring and download of data shall be also incorporated.

- Remote Server and Software for centralized Internet monitoring system shall be also provided for download and analysis of cumulative data of all the plants  and  the  data  of  the  solar  radiation and temperature monitoring system.

- Ambient / Solar PV module back surface temperature  shall  be  also monitored on continuous basis.

- Simultaneous monitoring of DC and AC  electrical  voltage,  current,  power,  energy  and other data  of  the  plant  for  correlation  with  solar  and environment data shall be  provided.

- Remote Monitoring and data acquisition through Remote Monitoring System software at the owner /APEPDCL location with latest software/hardware configuration and service connectivity for online / real time data monitoring/control complete to be supplied and operation and maintenance/control to be ensured by the supplier. Provision for interfacing these data on [NAME OF THE ORGANISATION] server and portal in future shall be kept.

### TRANSFORMER “IF REQUIRED” & METERING:

- Dry/oil  type  relevant kVA, 11kV/415V, 50 Hz Step up along with all protections, switchgears, Vacuum circuit breakers, cables etc. along with required civil work.

- The electronic energy meters as per the statutory requirements of APEPDCL shall be installed for the measurement of import/Export of energy & billing shall be as directed by APEPDCL/APERC/GOAP and amended from time to time. The bidder must take approval/NOC from the APEPDCL for the connectivity, technical feasibility, and  synchronization  of  SPV  plant  with  distribution network and submit the same to APEPDCL before commissioning of SPV plant.

- Reverse power relay shall be provided by bidder (if necessary), as per the APEPDCL requirement.

### PROTECTIONS

The system should be provided with all necessary protections like earthing, Lightning, and grid islanding as follows:

    - 8.14.1 LIGHTNING PROTECTION

The SPV power plants shall be provided with lightning &overvoltage protection. The main aim in this protection shall be to reduce the over voltage to a tolerable value before it reaches the PV or other sub system components. The source of over voltage can be lightning, atmosphere disturbances  etc.  The  entire  space  occupying  the  SPV   array shall be suitably protected against Lightning by deploying required number of Lightning Arrestors. Lightning protection should be provided as per IEC 62305 standard. The protection against induced high-voltages shall be provided by the use of metal oxide varistors (MOVs) and suitable earthing such that induced transients find an alternate route to earth.

    - 8.14.2 SURGE PROTECTION

Internal surge protection shall consist of three MOV type surge-arrestors connected from +ve and –ve terminals to earth (via Y arrangement)

    - 8.14.3 EARTHING PROTECTION

      - Each array structure of the PV yard should be grounded/ earthed properly as per IS:3043- 1987. In addition the lighting arrester/masts should also be earthed inside the array field. Earth Resistance shall be tested in presence of the representative of Department APEPDCL/User as and when required after earthing by calibrated earth tester. PCU, ACDB and DCDB should also be earthed properly.

      - Earth resistance shall not be more than 5 ohms. It shall be ensured that all the earthing  points are bonded together to make them at the same potential.

### 8.15 GRID ISLANDING:

    - In the event of a power failure on the electric grid, it is required that any independent power-producing inverters attached to the grid turn off in a short period of time. This prevents the DC-to-AC inverters from continuing to feed power into small sections of the grid, known as “islands.” Powered islands present a risk to workers who may expect the area to be unpowered, and they may also damage grid-tied equipment. The Rooftop PV system shall be equipped with islanding protection. In addition to disconnection from the  grid (due to islanding protection) disconnection due to under and over voltage conditions shall also be provided.

    - A manual disconnect 4pole isolation switch beside automatic disconnection to grid would have to be provided at utility end to isolate the grid connection by the utility personnel to carry out any maintenance. This switch shall be locked by the utility personnel

### 8.16 CABLES

Cables   of   appropriate   size   to   be   used   in   the   system	shall  have  the  following characteristics:

    - Shall meet IEC 60227/IS 694, IEC 60502/IS1554 standards

    - Temp. Range: –10oC to +80oC.

    - Voltage rating 660/1000V

    - Excellent resistance to heat, cold, water, oil, abrasion, UV radiation

    - Flexible

    - Sizes of cables between array interconnections, array to junction boxes, junction boxes to Inverter etc. shall be so selected to keep the voltage drop (power loss) of the entire solar system to the minimum. The cables (as per IS) should be insulated with a special grade PVC compound formulated for outdoor use.

    - Cable Routing/ Marking: All cable/wires are to be routed in a GI cable tray and suitably tagged and marked with proper manner by good quality ferule or by other means so that the cable easily identified.

    - The Cable should be so selected that it should be compatible up to the  life of the solar  PV panels i.e. 25years.

    - The ratings given are approximate. Bidder to indicate size and length as per system design requirement. All the cables required for the plant provided by the bidder.  Any change in cabling sizes if desired by the bidder/approved after citing appropriate reasons. All cable schedules/layout drawings approved prior to installation.

    - Multi   Strand,   Annealed   high   conductivity   copper   conductor   PVC   type   „A‟ pressure extruded insulation or XLPE insulation. Overall PVC/XLPE insulation for UV protection Armored cable for underground laying. All cable trays including covers to be provided. All cables conform to latest edition of IEC/ equivalent BIS Standards as specified below: BoS item / component Standard Description Standard Number Cables General Test and Measuring Methods, PVC/XLPE insulated cables for working Voltage up to and including 1100 V ,UV resistant for outdoor installation IS /IEC 69947.

    - The size of each type of DC cable selected shall be based on minimum voltage drop however; the maximum drop shall be limited to 1%.

    - The size of each type of AC cable selected shall be based on minimum voltage drop however; the maximum drop shall be limited to 2 %.

### 8.17	CONNECTIVITY

The maximum capacity for interconnection with the grid at a specific voltage level shall be as specified in the Distribution Code/Supply Code of the State/ AP solar rooftop policy amended from time to time. Following criteria have been suggested for selection of voltage level in the distribution system for ready reference of the solar suppliers.

| Plant Capacity | Connecting voltage |
| --- | --- |
| Up to 3 kW | 230V-single phase or 415V-three phase at the option of the consumer |
| Above 3kW and up to 10 kW | LT three phase |

### TOOLS & TACKLES AND SPARES:

- After  completion   of   installation   &   commissioning   of   the   power   plant, necessary tools & tackles are to be provided free of cost by the bidder for maintenance purpose. List of tools and tackles to be supplied by the bidder for    approval    of    specifications.

- A list of requisite spares in  case  of  PCU/inverter  comprising  of  a  set  of control logic cards, IGBT driver cards etc. Junction Boxes. Fuses, MOVs / arrestors, MCCBs etc  along  with spare set of PV modules be indicated, which shall be  supplied  along  with  the equipment. A minimum set of spares shall be maintained in the plant itself for the entire period of warranty and Operation & Maintenance which upon its use shall be replenished

### DANGER BOARDS AND SIGNAGES:

Danger boards should be provided as and where necessary as per IE Act. /IE rules as amended up to date. Three signage shall be provided one each at battery – cum - control room,  solar  array  area  and   main   entry   from administrative block. Text of the signage may be finalized in consultation with APEPDCL/ owner.

### FIRE EXTINGUISHERS:

The fire fighting system for the proposed power plant for fire protection shall be consisting of:

- Portable fire extinguishers in the control room for fire caused by electrical short circuits

- Sand buckets in the control room

- The installation of Fire Extinguishers should confirm to TAC regulations and BIS standards. The fire extinguishers shall be provided in the control room housing PCUs as well as on the Roof or site where the PV arrays have been installed.

### DRAWINGS & MANUALS:

- Two sets of Engineering, electrical drawings and Installation and O&M manuals are to be supplied. Bidders shall provide complete technical data sheets for each equipment giving details of the specifications along with make/makes in their bid along with basic design of the power plant and power evacuation, synchronization along with protection equipment.

- Approved ISI and reputed makes for equipment be used.

- For complete electro -mechanical works , bidders shall sup pl y complete design, details and drawings for approval to APEPDCL/owners before progressing with the installation work

### PLANNING AND DESIGNING:

    - The bidder should  carry  out  Shadow  Analysis  at  the  site  and  accordingly design strings  & arrays layout considering optimal usage of space, material and labour. The bidder should submit    the array layout drawings along with Shadow Analysis Report to APEPDCL /Owner for approval.

    - APEPDCL reserves the right to modify the landscaping design, Layout and specification  of sub-systems and components at any stage as per local site conditions/requirements.

    - The bidder shall submit  preliminary  drawing  for  approval  &  based  on  any modification or recommendation, if any. The bidder submits three sets and soft copy in CD of final drawing for formal approval to proceed with construction work.

### DRAWINGS TO BE FURNISHED BY BIDDER AFTER AWARD OF CONTRACT

    - The Contractor shall furnish the following drawings Award/Intent and obtain approval

    - General arrangement and dimensioned layout

    - Schematic drawing showing the requirement of SV panel, Power conditioning Unit(s)/  inverter, Junction Boxes, AC and DC Distribution Boards, meters etc. iv. Structural drawing along with foundation details for the structure.

    - Itemized bill of material for complete SV plant covering all the components and associated accessories.

    - Layout of solar Power Array

    - Shadow analysis of the roof

  - SOLAR PV SYSTEM ON THE ROOFTOP FOR MEETING THE ANNUAL ENERGY

REQUIREMENT :-

The Solar PV system on the rooftop of the selected buildings will be installed  for meeting upto 90% of the annual energy requirements depending upon the area of rooftop available and the remaining energy requirement of the buildings will be met by drawing power from grid at commercial tariff of DISCOM.

### SAFETY MEASURES:

The bidder  shall  take  entire  responsibility  for  electrical  safety  of  the installation(s)  including connectivity with the grid and follow all the safety rules & regulations applicable as per Electricity Act, 2003 and CEA guidelines etc.

### TEST CERTIFICATES AND REPORTS TO BE FURNISHED

Test Certificates / Reports from IECQ / NABL accredited laboratory for relevant IEC / equivalent BIS standard for quoted components shall be furnished. Type Test Certificates shall be provided for the solar modules and the solar grid inverter to provide evidence of compliance with standards as specified by Ministry of New and Renewable Energy (MNRE). APEPDCL reserves the right to ask for additional test certificates or (random) tests to establish compliance with the specified standards.

### 8.28       CONFIRMATION TO MNRE TECHNICAL SPECIFICATIONS AND STANDARDS

The Tenderer should ensure that all components and systems used under this Scheme shall strictly adhere to the Technical Specifications and Guidelines issued by MNRE, and as amended from time to time.

# TECHNICAL BID

# TECHNICAL BID FORMAT

All pages of the Technical Bid shall be organised section-wise, annexed with proof documents, serially numbered and stitched/or spiral bound intact and submitted) Loose pages shall not be accepted.

# GENERAL PARTICULARS OF TENDERER

| SL. | PARTICULARS |  |  |  | TO BE FUNISHED BY THE TENDERER |
| --- | --- | --- | --- | --- | --- |
| 1 | Name of Tenderer/Firm |  |  |  |  |
| 2 | Registered Office & Postal Address |  |  |  |  |
| 3 | E-mail address for communication & Website |  |  |  |  |
| 4 | Telephone/ Fax No. |  |  |  |  |
| 5 | Name, designation, address, contact number and Email of the representative of the tenderer to whom all references shall be made. |  |  |  |  |
| 6 | Nature of the firm (Individual/ Partnership / Consortium/ Pvt. Ltd /Public Ltd. Co. /Public Sector, etc.) Attach attested copy of Registration & Partnership deed/ Memorandum of Association, Year of Incorporation |  |  |  |  |
| 7 | Amount and particulars Money Deposited. | of | the | Earnest |  |
| 8 | Annual Turnover for last five years i.e 2015 -2020 (Attach balance sheets from CA in this regard) |  |  |  |  |
| 9 | Net worth of the company as on 31.03.2020 (Attach CA certificate in this regard) |  |  |  |  |

| 10 | Name and address of the Indian/foreign collaboration if any. |  |
| --- | --- | --- |
| 11 | PAN NO (Copy of certificate to be enclosed) |  |
| 12 | GST No. (copies of certificates to be attached) |  |
| 13 | Has the Bidder /firm ever been debarred by any Govt Dept /institution/DISCOM for undertaking any work? |  |
| 14 | Any other information attached by the Bidder (Details of Annexure / page no. where its enclosed) |  |
| 15 | Does Bidder have any relative Working in APEPDCL? If yes state the Name and designation. |  |
| 16 | Whether company is MSME as on the bidding date. In case of MSME Company Aadhar Memorandum Particulars to be indicated. |  |
| 17 | Bank Account Details, For Bank A/c Details a copy of Cancelled Cheque to be enclosed. |  |

- DETAILS ABOUT THE COMPONENTS TO BE USED

| S. No | Description | Name of Manufacturer(s) | Manufacturing Plant address |
| --- | --- | --- | --- |
| 1 | Solar PV Modules |  |  |
| 2 | Grid Tied Inverter/PCU |  |  |

Enclose the Data Sheets of Solar PV Modules and Grid Tied Inverters proposed to be used

# DETAILS OF EXPERIENCE

Please fill in information about grid connected/off grid Solar PV Systems installed in the last Five years.

| Sl. No | Description | FY 2015-16 | FY 2016-17 | FY 2017-18 | FY 2018-19 | FY 2019-20 |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Grid Connected Solar PV Plants in KWp |  |  |  |  |  |

# Documentary Evidences to be submitted:

  - Work Order Copies/Project Sanction Letter /Invoice

  - Project Completion Report/Certificate clearly showing the date of commissioning

  - Annual Financial Turnover /Net-worth

# DETAILS ABOUT THE BLACKLISTING, IF ANY

Information on litigation history in which Bidder is involved.

- Whether black listed/ Debarred/Suspended from execution of work.

- Other litigations. If any including Court litigations Arbitrations etc.

| Department and Concerned officer | Other party (ies) | Case of dispute. | Amount involved. | Remarks showing present status. |
| --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 |

Signature of the authorised person: Name of the authorised person: Designation:

Name and Address of Bidder Stamp of bidder

FINANCIAL BID

The cost of SPV power plants shall include their respective components as per their respective technical specification, including cables, MCBs, switches, fuses etc., as per the site requirement inclusive of 5 years CMC charges, Online monitoring ,insurance and shall be a lump-sum turnkey price:

| Project Category | Turn-key Price of Grid Connected Rooftop Solar PV Power Plant as per MNRE/CEIG /DISCOM Specifications (Rs./Wp) (Rate per Wp is to be quoted) | (Rs./Wp) IN WORDS (Rate per Wp is to be quoted) |
| --- | --- | --- |
| 1KWp |  |  |
| Above 1 KWp upto 2KWp |  |  |
| Above 2 KWp upto 3KWp |  |  |
| Above 3 KWp upto 10KWp |  |  |

Note:

  - Total cost quoted above is without deducting any incentive.

  - The quoted price is inclusive of all taxes, duties, freight with 5 years insurance up to site, for installation and commissioning within the jurisdiction of  APEPDCL, incl. AMC for 5yrs period after commissioning.

  - The price quoted shall be in both figures and words, rounded to one decimal point. Price quoted after first decimal point, if any, shall not be considered.

  - In case of discrepancy in the Price quoted between Words and Figures, the rates mentioned in words only shall be considered .

  - The Tenderer must quote for all the category of Projects.

Signature of the authorised person:

Name of the authorised person:

Designation:

Name and Address of Bidder and Stamp of bidder

# FORMATS

Format -1

BIDDERS UNDERTAKING COVERING LETTER

(Letter shall be submitted on Bidder(s) Letter Head)

Ref No:	Date:

To

The Chief General Manager, Energy Conservation, Energy Audit & Solar

Eastern Power Distribution Company of A.P Ltd. (APEPDCL)

Corporate  Office , P&T, Colony, Seethammadhara, Visakhapatnam Visakhapatnam District

Pin: 530 013.

Dear Sir/ madam,

Sub:	EMPANELMENT FOR DESIGN,SUPPLY, INSTALLATION, TESTING & COMMISSIONING and Integrated Comprehensive Maintenance for 5 Years of Grid Connected Rooftop Solar Photovoltaic (PV) Power Units of capacity 1 KWp to 10 KWp for Residential sector in APEPDCL under capex mode- reg.

Tender Reference: RFS No. CGM/EC,EA& Solar/GM(EC& SOLAR)/01/2020-21,Dt.02.12.2020

***

- We have examined the Tender for DESIGN,SUPPLY, INSTALLATION, TESTING & COMMISSIONING and Integrated Comprehensive Maintenance for 5 Years of Grid Connected Rooftop Solar Photovoltaic (PV) Power Units as specified in the Tender. We undertake to meet the requirements and services as required and as set out in the Tender document.

- We attach our Technical Bid in sealed covers as required by the Tender in full conformity with the said Tender.

- We have read the provisions of Tender and confirm that these are acceptable to us. We further declare that additional conditions, variations, deviations, if any, found in our response shall not be given effect to.

- We undertake, if our Bid is accepted, to adhere to the requirements as specified in the Tender or such modified plan as may subsequently be agreed.

- We agree to unconditionally accept all the terms and conditions set out in the Tender document and also agree to abide by this Bid response for a period as mentioned in the Tender from the date fixed for bid opening and it shall remain binding upon us with full force and virtue, until within this period a formal contract is prepared and executed, this Bid response, together with your written acceptance thereof in your notification of empanelment, shall constitute a binding contract between us and APEPDCL.

- We affirm that the information contained in the Technical Bid or any part thereof, including its schedules, and other documents, etc., delivered or to be delivered to APEPDCL is true, accurate, and complete. This proposal includes all information necessary to ensure that the statements therein do not in whole or in part mislead APEPDCL as to any material fact.

- We also agree that you reserve the right in absolute sense to reject all or any of the products/ service specified in the bid response without assigning any reason whatsoever.

- It is hereby confirmed that I/We are entitled to act on behalf of our company/ organization and empowered to sign this document as well as such other documents, which may be required in this connection.

- We agree to use only indigenous PV modules (using domestic manufactured solar cells) in this project as specified by MNRE.

- We also declare that our Company/Organisation is not blacklisted by any of the State or Central Government and organisations of the State or Central Government.

- We undertake to use the BOS components other than PV Modules and Solar grid tie Inverters as per the standards stipulated.

Signature of the authorised person: Name of the authorised person:

Designation: Name and Address of Bidder

Stamp of bidder

# Format -2:

# CERTIFICATE AS TO AUTHORISED SIGNATORIES

I, certify that I am (Name) …………………………… (Designation) …………………, and that (Name)…………………………………… who signed the above Bid has been duly authorized to sign the same on behalf of our Organisation.

Date:

Signature:

Seal:

# Format – 3:

# FORMAT FOR BANK GUARANTEE FOR - EARNEST MONEY DEPOSIT

This deed of Guarantee made on.................... day of Month & Year by Name & Address of the bank (hereinafter called the “GUARANTOR”) on the one part, on behalf of M/s Name & address of the Firm (hereinafter called the “Firm”) ) in favour of The Chief General Manager, Energy Conservation, Energy Audit & Solar/ APEPDCL, Visakhapatnam on the following terms and conditions.

Whereas the FIRM is submitting its tender for (Name of the work) and this guarantee is being made for the purpose of submission of Earnest money deposit with the tender document.

Know all people by these presents that the GUARANTOR, hereby undertake to indemnify and keep APEPDCL indemnified up to the extent of Rs .2,00,000/- ( Rs. Two Lakhs ) during the validity of this bank guarantee and authorize  APEPDCL to recover the same directly from the GUARANTOR. This bank guarantee herein contained shall remain in full force and effect till the expiry of its validity or till any extended period (if extended by the bank on receiving instructions from FIRM.). The liability under the guarantee shall be binding on the GUARANTOR or its successors.

Whereas the GUARANTOR further agrees that their liability under this guarantee shall not be affected by any reason of any change in the offer or its terms and conditions between the FIRM and APEPDCL with or without the consent or knowledge of the GUARANTOR.

Whereas the GUARANTOR further agrees to pay guaranteed amount hereby under or part thereof, on receipt of first written demand whenever placed by APEPDCL during the currency period of this guarantee. The GUARANTOR shall pay APEPDCL immediately without any question, demure, reservation or correspondence.

Whereas the GUARANTOR hereby agrees not to revoke this guarantee bond during its currency period except with the previous consent of APEPDCL in writing.

Notwithstanding anything contained herein

- Our liability under this bank guarantee shall not exceed Rs.2,00,000/- ( Two Lakhs).

- This Bank guarantee shall be valid up to …………...

- We are liable to pay the guaranteed amount or any part thereof under this bank guarantee only and only against the written claim or demand on or before ………….. Sealed with the common seal of the bank on this ……….day of Month and Year

# Witness :

# 1.

2

(Signature and seal of Bank)

Format -4

DECLARATION

(on Rs.100/- non-judicial stamp paper)

I / WE ………………………………………………………………. have gone through carefully all the Tender conditions and solemnly declare that I / we will abide by any penal action such as disqualification or black listing or determination of contract or any other action deemed fit, taken by, the Department against us, if it is found that the statements, documents, certificates produced by us are false / fabricated.

I / WE hereby declare that, I / WE have not been blacklisted / debarred / Suspended / demoted in any Government Department in any State due to any reasons.

# Signature of the Tenderer

Format -5

DECLARATION BY THE TENDERER

I/We

…………………………………………………………………………………………………

…………….

(Hereinafter referred to as Tenderer) being desirous of tendering for the work, under this tender and having fully understood the nature of the work and having carefully noted all the terms and conditions, specifications etc. as mentioned in the tender document do hereby declare that

- The tenderer is fully aware of all the requirements of the tender document and agrees with all provisions of the tender document and accepts all risks, responsibilities and obligations directly or indirectly connected with the performance of the tender.

- The Tenderer is fully aware of all the relevant information for proper execution of the proposed work, with respect to the proposed place of works/ site, its local environment, approach road and connectivity etc. and is well acquainted with actual and other prevailing working conditions, availability of required materials and labour etc. at site.

- The Tenderer is capable of executing and completing the work as required in the tender and is financially solvent and sound to execute the tendered work. The tenderer is sufficiently experienced and competent to perform the contract to the satisfaction of APEPDCL. The Tenderer gives the assurance to execute the tendered work as per specifications, terms and conditions of the tender on award of work.

- The Tenderer has no collusion with other Tenderers, any employee of APEPDCL or with any other person or firm in the preparation of the tender.

- The Tenderer has not been influenced by any statement or promises by APEPDCL or any of its employees but only by the tender document.

- The Tenderer is familiar with all general and special laws, acts, ordinances, rules and regulations of the Municipal, District, State and Central Government that may affect the work, its performance or personnel employed therein.

- The Tenderer has never been debarred from similar type of work by any Government Undertaking /Department. (An undertaking on Non-Judicial Stamp paper worth of Rs. 100/- in this regard shall be submitted)

- The Tenderer accepts that the earnest money / security deposit may be absolutely forfeited by APEPDCL if the selected bidder fails to sign the contract or to undertake the work within stipulated time.

- This offer shall remain valid for acceptance for 6 (Six) months from the proposed date of opening of Tender.

- All the information and the statements submitted with the tender are true and correct to the best of my knowledge and belief.

# Signature of Tenderer

Format -6

MODEL FORM OF AGREEMENT

To be executed on a Rs.200- Non-judicial Stamp paper of Andhra Pradesh jurisdiction by the Successful Bidder for DESIGN,SUPPLY, INSTALLATION, TESTING & COMMISSIONING and Integrated Comprehensive Maintenance for 5 Years of Grid Connected Rooftop Solar Photovoltaic (PV) Power Units of capacity 1 KWp to 10 KWp for Residential sector in APEPDCL(NO FIGURES IN NUMERALS OR WORDS SHALL BE FILLED UP IN THIS SAMPLE FORM AT THE TIME OF SUBMISSION OF TENDER)

# AGREEMENT

This Agreement is entered into at Visakhapatnam on the ............... day of 	2020 between Eastern Power Distribution Company of A.P Ltd (APEPDCL) having its Regd. Office at P&T Colony, Seethammadhara, Visakhapatnam – 530 013, Visakhapatnam District, Andhra Pradesh State, India hereinafter referred to as "APEPDCL" (Which term shall mean and include its successors and permitted assigns) and ................., a Company registered under …………………and having its Registered office at .............................. hereinafter referred to as the “Installer” (Which term shall mean and include its successors and permitted assigns)

Whereas APEPDCL invited a tender vide RFS No. CGM/EC,EA& Solar/GM(EC& SOLAR)/01/2020-21,Dt.02.12.2020 for Empanelment of DESIGN,SUPPLY, INSTALLATION, TESTING & COMMISSIONING and Integrated Comprehensive Maintenance for 5 Years of Grid Connected Rooftop Solar Photovoltaic (PV) Power Units of capacity 1 KWp to 10 KWp for Residential sector in from the date of synchronization of Grid connected SPV Rooftop Systems in the Jurisdiction of APEPDCL.

This document on having been signed by both the parties shall constitute a binding contract between the parties and shall remain in force for a period of five years. But in the event of any breach of the Contract at any time on the part of the Installer, the contract shall be terminated by APEPDCL without compensation to the Installer. The contract may also be put to an end at any time by the APEPDCL upon giving seven days notice to the Installer. The Installer agrees for Supply, Installation, and Commissioning of  SPV Rooftop within 60 months and warranty as per clause 7.13 and as per the Terms & Conditions given below.

- Installation & Completion Schedule

The entire work involving DESIGN,SUPPLY, INSTALLATION, TESTING & COMMISSIONING of Grid Connected Rooftop Solar Photovoltaic (PV) Power Units of capacity 1 KWp to 10 KWp for Residential sector in APEPDCL shall be completed within 45 to 90 days based on capacity of the system from the date of issue of work order by the purchaser.

- Service:

Empanelled Installer shall have 2 service centers in the jurisdiction of APEPDCL. In case if it is not economically viable for an individual Empanelled Installer, then Group of three (3) or less Empanelled Installers can establish service center jointly . The service center details shall be made available at the time of entering into agreement with APEPDCL and the same will be displayed  on the website of APEPDCL. These service centres have to provide services to the RTS owners within the timelines decided by the DISCOMs, free of cost for first five years (Warranty period) of commissioning the RTS.

- The Installer shall visit the site at least once in a quarter, to attend routine maintenance, during the 5 years warranty period. However, in case of malfunctioning of the system, the bidder shall attend for rectification of defects within 5 working days from the date of lodging complaint. if the empanelled vendors still find violating the provisions of the integrity pact provided in the bid during the installation he execution of plant and/or In case the systems are not as per standards, non-functional on account of poor quality of installation, or non-compliance of CMC, then empanelment of such vendors are liable to be cancelled. In addition to this, APEPDCL/MNRE reserves the right to award punishment to such empanelled vendor, which includes forfeiture of their submitted Performance Security and/or blacklisting. Such Vendor will be barred from participating in the tenders for a period of 1 year.

- Installation and Commissioning locations:

The Grid Connected Solar Rooftop Power Plants shall be installed and commissioned anywhere in Jurisdiction of APEPDCL.

- The validity of Empanelment and the price accepted will be for 12 months.

- The following documents shall be deemed to form and be read and constructed as part of this Contract.

  - Technical Specifications of MNRE/APEPDCL/CEIG/CEA

  - Tender Terms and Conditions

  - Amendments if any issued by APEPDCL for the Tender document

  - Corrigendum/Clarifications issued by APEPDCL for the Tender document

  - Detailed final offer of the Successful Bidder

  - Correspondence made by APEPDCL to the successful Bidder from time to time during the period of the contract.

- Waiver of any terms and conditions by APEPDCL / Purchaser in writing shall not have the effect of waiving or abandoning other terms and conditions of the contract.

- (a)	 Unless otherwise provided in the Contract, any notice, request, consent or other communication

given     or required to be given hereunder shall be given by mailing the same by registered

mail, postage prepaid to APEPDCL at its registered office.

(b) 	Any notice to the Installer shall be deemed to be sufficiently served, if given or left in writing at their usual or last known place of abode or business In case of failure by the Installer to commission the solar Rooftop systems within the period specified as per the schedule or in case of installations made by them, not being of the stipulated quality and specifications, APEPDCL shall have the power to reject any such installations.

- APEPDCL is no way responsible for any dispute arising between the Installer & Purchaser.

Subject to the above, the Courts of AP jurisdiction alone only shall have jurisdiction in the matter of empanelment.

In Witness whereof the parties hereto have signed on the day, month and year above written in the presence of

# For and on behalf of	For and on behalf of

APEPDCL	Installer

Name	Name

Designation	Designation

Seal	Seal

# Witnesses:	Witnesses:

1.

2.

Format -7

FORMAT FOR SECURITY DEPOSIT

(To be on non-judicial stamp paper of appropriate value as per Stamp Act relevant to place of execution.)

In consideration of the ----- [Insert name of the Bidder] (hereinafter referred to as selected Agency) submitting the response to Bid document inter alia for 	(Name of Work), in response to the Bid document dated………… issued by APEPDCL (hereinafter referred to as Authorised Representative) having its Registered Office at Corporate Office, P&T Colony, Seethammadhara, Visakhapatnam district, Andhra Pradesh and Authorised Representative considering such response to the Bid document of ………[insert the name of the selected Agency] (which expression shall unless repugnant to the context or meaning thereof include its executers, administrators, successors and assignees) and the Agency and issuing Letter of Allocation No ------- to (Insert Name of selected Agency) as per terms of Bid document and the same having been accepted by the selected agency.

As per the terms of the  Bid document, the    [insert name  & address of bank]    hereby agrees unequivocally, irrevocably and unconditionally to pay to the APEPDCL, Corporate Office, Visakhapatnam district forthwith on demand in writing from The  Chief General Manager, Energy Conservation, Energy Audit & Solar, APEPDCL or any Officer authorised by it in this behalf, any amount of upto and not exceeding Rupees ----- [Total Value] only, on behalf of M/s [Insert name of the selected Agency / Project Company]

This guarantee shall be valid and binding on this Bank up to and including……….. and shall not be terminable by notice or any change in the constitution of the Bank or the term of contract or by any other reasons whatsoever and our liability hereunder shall not be impaired or discharged by any extension of time or variations or alternations made, given, or agreed with or without our knowledge or consent, by or between parties to the respective agreement.

Our Guarantee shall remain in force until…………….[Insert date corresponding to  the Bid document] shall be entitled to invoke this Guarantee till……….…………….[Insert date corresponding to thirty (30) days after the validity of the Performance Bank Guarantee.

The Guarantor Bank hereby agrees  and acknowledges that …………….[Insert name of the APEPDCL with which Agreement will be signed] shall have a right to invoke this BANK GUARANTEE in part or in full, as it may deem fit.

The Guarantor Bank hereby expressly agrees that it shall not require any proof in

addition to the written demand by ……………., made in any format, raised at the above mentioned address of the Guarantor Bank, in order to make the said payment to………… The Guarantor Bank shall make payment hereunder on first demand without restriction or conditions and notwithstanding any objection by -------------[Insert name of the selected Agency / Project Company as applicable] and/or any other person. The Guarantor Bank shall not require [Insert name of the APEPDCL with which Agreement will be signed], to justify the invocation of this BANK GUARANTEE, nor shall the Guarantor Bank have any recourse against…………….[Insert name of the APEPDCL with which Agreement will be signed] in respect of any payment made hereunder

This BANK GUARANTEE shall be interpreted in accordance with the laws of India and the courts at Andhra Pradesh shall have exclusive jurisdiction.

The Guarantor Bank represents that this BANK GUARANTEE has been established in such form and with such content that it is fully enforceable in accordance with its terms as against the Guarantor Bank in the manner provided herein.

This BANK GUARANTEE shall not be affected in any manner by reason of merger, amalgamation, restructuring or any other change in the constitution of the Guarantor Bank.This BANK GUARANTEE shall be a primary obligation of the Guarantor Bank and Accordingly,

APEPDCL shall not be obliged before enforcing this BANK GUARANTEE to take any action in any court or arbitral proceedings against the selected Agency / Project Company, to make any claim against or any demand on the selected Agency / Project Company or to give any notice to the selected Agency / Project Company or to enforce any security held by APEPDCL or to exercise, levy or enforce any distress, diligence or other process against the selected Agency / Project Company .

The Guarantor Bank  acknowledges  that  this  BANK  GUARANTEE  is  not  personal to APEPDCL and may be assigned, in whole or  in  part,  (whether absolutely or by way of security) by APEPDCL to any entity to whom APEPDCL is entitled to assign its rights and obligations under the Agreement.

Notwithstanding anything contained herein above, our liability under this Guarantee is restricted to Rs. 	(Rs. 	only) and it shall remain in force until ……………..…………….[Insert date corresponding to the Bid document]. We are liable to pay the guaranteed amount or any part thereof under this Bank Guarantee only if …………….[Insert name of the APEPDCL with which Agreement will be signed] serves upon us a written claim or demand.

Signature

Name 	, Power of Attorney No.

For

[Insert Name of the Bank] 	, Banker's Stamp and Full Address.

Dated this 	day of 	, 20 	 Witness:

1. ……………………………………. Signature

Name and Address

2. …………………………………..

Signature

Name and Address Note:

The Stamp Paper should be in the name of the Executing Bank and of appropriate value.

# Format -8

# CHECKLIST TO ACCOMPANY THE TENDER

| S. No | Description |  |  |  |  |  | Whether Uploaded or not | Page No. (see Note below) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 |  |  |  |  |  | 3 | 4 |
| 1 | Demand draft toward requisite Earnest Money Deposit (issued by any Nationalised bank) or exemption document or Bank Guarantee. |  |  |  |  |  | Yes /No |  |
| 2 | Crossed demand draft towards Tender Processing fee Rs.25,000 + GST @ 18% |  |  |  |  |  | Yes /No |  |
| 3 | Copy of PAN card |  |  |  |  |  | Yes /No |  |
| 4 | Copy of latest Income Tax Clearance returns submitted along with proof of receipt (Latest SARAL form). |  |  |  |  |  | Yes /No |  |
| 5 | CA Certificate for the Turnover for the period 2015- 2020 (Year wise) |  |  |  |  |  | Yes /No |  |
| 6 | CA certificate for Net worth as on 31.03.2020 |  |  |  |  |  | Yes /No |  |
| 7 | Copies of GST Registration Certificate. |  |  |  |  |  | Yes /No |  |
| 8 | Latest GST clearance certificate. |  |  |  |  |  | Yes /No |  |
| 9 | Availability personnel | of | local | service | centres/ | technical | Yes /No |  |
| 10 | Information on litigation history in which Bidder is involved. |  |  |  |  |  | Yes/No |  |
| 11 | Any other documents/certificate as specified in tender conditions |  |  |  |  |  | Yes /No |  |
| 12 | Experience Certificate |  |  |  |  |  | Yes /No |  |
| 13 | Declarations as per the formats |  |  |  |  |  | Yes /No |  |

Notes:

1. All the statements copies of the certificates, documents etc., enclosed to the Technical bid shall be given page numbers on the right corner of each certificate, which will be indicated in column (4) against each item. The statements furnished shall be in the formats appended to the tender document.

2. 	The information shall be filled-in by the Bidder in the check list, as applicable and shall be enclosed to the Technical bid for the purposes of verification as well as evaluation of the Bidders Compliance to the qualification criteria as provided in the Tender document.

The bidder shall sign on all the statements, documents, certificates by him, owning responsibility for their correctness/authenticity.

Annexure - A

Undertaking/Self- Declaration for domestic content requirement fulfilment

(On a plain Paper)

This is to certify that M/S…………………………………………..[Company Name] has installed……………KW [Capacity] Grid Connected Rooftop Solar PV Power Plant for……………………………………………………………. [Consumer Name] at………………………. [Address] under sanction number……………………dated………………………………….…….[sanction date] issued by…………………………[DISCOM Name].

2. It is hereby undertaken that the PV modules installed for the above-mentioned project are

domestically manufactured using domestic manufactured solar cells. The details of installed PV

Modules are follows:

1. PV Module Capacity:

2. Number of PV Modules:

3. Sr No of PV Module

4. PV Module Make:

5. Purchase Order Number:

6. Purchase Order Date:

7. Cell manufacturer’s name

8. Cell GST invoice No

3. The above undertaking is based on the certificate issued by PV Module manufacturer/supplier while supplying the above-mentioned order.

4. I, ………………………on behalf of M/S………………………………………[Company

Name] further declare that the information given above is true and correct and nothing has been

concealed therein. If anything is found incorrect at any stage then the due Central Financial

Assistance (CFA) that I have not charged from the consumer can be withheld and appropriate

action may be taken against me and my company for wrong declaration. Supporting documents

and proof of the above information will be provided as and when requested by MNRE.

(Signature With official Seal)

For M/S…………….……………………………..

Name:………..……………………………………

Designation:…………..…………………………..

Phone:………………………………….…………

Email:………….…………………………………

Annexure - B

PROJECT REPORT FORMAT

Format for Summary Project Report for Grid Connected Rooftop:

- Name of Bidder	:

- RfS No.	:

- Project details (Site location&Address)	:

- Name of the beneficiary	:

- Size of Plant(in KW)	:

#### Specifications of the Components and Bill of Material/ Quantities:

| S. No. | Component | Specifications Quantity | Make |
| --- | --- | --- | --- |
| A | Solar PV module |  |  |
| A.1 | Aggregate Solar PV capacity (kWp) |  |  |
| B | Grid Tie inverter (Type and Capacity) |  |  |
| B.1 | Aggregate Inverter capacity (kVA) |  |  |
| C | Module mounting structure |  |  |
| D | Array Junction Box |  |  |
| E | AC Distribution Board |  |  |
| F | Cable (All type) | DC: AC: |  |
| G | Earthing Cable/ Strip |  |  |
| H | Lightening Arrestor |  |  |
| I | Earthing Pits (No.) | LA: DC: AC: |  |
| J | Online monitoring system |  |  |
| K | Any other component |  |  |

- Expected Output/annum

- Respective drawings for module layout, electrical wiring connections, earthing, components etc.

- Connectivity details with grid and metering arrangement (with sketch diagram)

- Copy of electricity bill of the beneficiary and consumer number

- Documentary Proof regarding beneficiary type

- Any other information

Annexure - C

Project Completion Report for Grid-Connected Rooftop

| Financial year: |  |  |  |
| --- | --- | --- | --- |
| Sanction Letter No. : |  |  |  |
| Proposal Title : |  |  |  |
| Installed by agency : |  |  |  |
| Title of the Project: |  | SPV Capacity (kWp): |  |
| Category of the organization/ beneficiary: |  | Name of the contact person: |  |
| Address of contact person: |  |  |  |
| State: |  | District/ City: |  |
| Mobile: |  | Email: |  |
| Aadhaar Card Number (For Residential) |  | Latitude: |  |
|  |  | Longitude: |  |
| DISCOM |  | Sanction Load |  |
| CA No. |  |  |  |

| Technology Description & System Design/Specification |  |  |  |
| --- | --- | --- | --- |
| (Compliance to BIS/ IEC Standards is mandatory) |  |  |  |
| 1. Solar PV Module: |  |  |  |
| Power of each PV Module / Nos.(Wp)* / Make |  |  |  |
| Cumulative Capacity of Modules (kWp): |  |  |  |
| Solar cell technology: |  | Tilt Angle of Modules: |  |
| Module efficiency (in %) : |  | Azimuth |  |
| Indigenous or imported (Cell) |  | RFID passed inside or outside: |  |
| Indigenous or imported (Module) |  | * Supported by Appropriate documentation |  |
| 2. Inverters: |  |  |  |
| Type of inverter : |  |  |  |
| Power of each PCU/Nos. of inverters (KVA)* /Make |  |  |  |
| Capacity/Power of PCU/inverters (KVA) : |  | Type of Charge Controller /MPPT |  |
| Inverter efficiency (in %) |  |  |  |
| Grid connectivity level phase | Single Phase/ Three Phase | Grid connectivity level Voltage | 220 V/ 415 V |
| 3. Mounting Structures |  |  |  |
| Type |  | Surface Finish |  |
| Material |  | Wind Speed Tolerance |  |
| 4. Cables: |  |  |  |
| DC Cable Make |  | Size |  |
| AC Cable Make (Inverter to ACDB) |  | Size |  |
| AC Cable Make (ACDB to Electric Panel) |  | Size |  |
| Conductor |  | Insulation/ sheath | PVC / XLPE |
| 5. JUNCTION BOX & DISTRIBUTION BOARDS |  |  |  |
| ACDB |  | Nos. |  |
| DCDB |  | Nos. |  |
| 6. EARTHING & LIGHTNING PROTECTION |  |  |  |
| EQUIPMENT EARTHING |  |  |  |
| AC (Nos.) |  | Earth Resistance |  |
| DC (Nos.) |  | Earth Resistance |  |
| LIGHTNING ARRESTORS (LA) |  |  |  |
| Type |  |  |  |
| LA (Nos.) |  | Earth Resistance |  |
| 7. Online Monitoring Mechanism: |  |  |  |
| Web Portal : |  |  |  |
| USER ID : |  | Password: |  |
| 8. Weather monitoring: |  |  |  |
| Solar Irradiance (Pyranomerter - Class IInd or better) |  | Temperature | Ambient & Module |
| Wind speed sensor |  |  |  |
| 9. Fire Fighting Device / System |  |  |  |
| 10. Danger Board |  |  |  |

Date:…………………………	(Signature of Vendor)

With Stamp

Annex:

  - Copy of System test & Earth test reports(annexed)

#### Commissioning Test Report: Solar Project ……. kW

InverterTesting(DC)Side:Nos.ofInverter	Nos.

| Inverter S. No. | Capacity | String 1: Voc | String 2: Voc | Remark |
| --- | --- | --- | --- | --- |

Inverter Testing (AC) Side – Single / Three Phase

| Inverter S. No. | Capacity | R – Y/ P- N | Y – B | B - R | R – N | Y – N | B - N | Remark |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

ACDB & Meter Panel Testing – Single / Three Phase

|  | R – Y/ P-N | Y – B | B – R | R – N | Y – N | B - N | Remark |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ACDB I/C (V) |  |  |  |  |  |  |  |
| ACDB O/G (V) |  |  |  |  |  |  |  |

EarthingPitDetails:Nos.ofEarthPit	Nos.

|  | Earthing AC | Earthing DC | Earthing LA | Remark |
| --- | --- | --- | --- | --- |
| Earth Test Value (Ohm) |  |  |  |  |

Date: …………………

Sign …………………………

Site Engineer

Annexure - D

(Subsidy Claim Letter on Company letter Head)

Ref No…………………	Date:……..

To, DISCOM

Sub: Claim Letter for release of subsidy for Solar Power Plant of …… kWp capacity installed at

……….

Ref:

- XXXSanction  letter No………………

Dear Sir,

This is in reference to DISCOM allocation and sanction letter, We,	(Name of Company) has successfully commissioned the	kWp capacity rooftop solar plant installed at

…………………………….. (Name, CA No. & Address Site).

As per the sanction order,	(Name of Company) is entitled to a subsidy of

INRs	,

post successful installation, commissioning and inspection of the rooftop Solar Power Plant. Therefore, kindly release the subsidy of INR	(Rs. In words) at the earliest.

Thanks and regards,

(Signature)

#### Signed and Stamp

Check List

Documents against Completion of Project

Name of Vendor:

Sanction letter No. :

Name of Beneficiary:

Installed Capacity:kW

| S. No. | Documents | Yes / NO | Page No. |
| --- | --- | --- | --- |
| 1. | Claim letter for Subsidy (Annexure D) |  |  |
| 2. | Solar System Warrantee Certificate for 5 / 25 years |  |  |
| 3. | Copy of Inspection report |  |  |
| 4. | Copy of PR Test report |  |  |
| 5. | Copy of Completion report |  |  |
| 6. | Copy of Solar System (Electrical side) testing report |  |  |
| 7. | Copy of Joint Completion certificate (JCR) |  |  |
| 8. | Solar PV module & Solar Inverter Serial No. |  |  |
| 9. | Solar PV module & Solar Inverter test sheet |  |  |
| 10. | Solar PV module & Solar Inverter warranty certificates |  |  |
| 11. | Solar PV plant Insurance Cover |  |  |
| 12 | PV System, Stand Pro, Final BOM, As built drawing |  |  |
| 13 | Metering Installation report |  |  |
| 14 | User name and Password of remote monitoring system along with Open API of data logger |  |  |

Signature

ANNEXURE - E

Joint Commissioning Report(JCR)

COMMISSIONING REPORT (PROVISIONAL) FOR GRID CONNECTED SOLAR

PHOTOVOLTAIC POWER PLANT

Certified that a Grid Connected SPV Power Plant of	KWp capacity has been installed at the

site…………………………………………………………………………………………………………………………………………………

………

………………………………………………………………………………………………………………………………………………………………

…	district	…………………………………………….	of

…………………………………………………………………………………………. which has been installed	by	M/S

…………………………………………………………………………………………………………

….. on ……………………………………………. The system is as per BIS/MNRE specifications. The system has been checked for its performance on ……………….............. with / without installation of meter and it is working satisfactorily. The system is suitable for installation of energy meters.

#### Signature of the beneficiary

Signature of the rep. of supplier- With name, seal and date

Signature of the DEE./AEE/AE With name, date and seal

Annexure F

Operation and Maintenance Guidelines of Grid Connected PV Plants

- For the optimal operation of a PV plant, maintenance must be carried out on a regular basis.

- All the components should be kept clean. It should be ensured that all the components are fastened well at their due place.

- Maintenance guidelines for various components viz. solar panels, inverter, wiring etc. are discussed below:

SOLAR PANELS

Although the cleaning frequency for the panels will vary from site to site depending on soiling, it is recommended that

  - The panels are cleaned at least once every fifteen days.

  - Any bird droppings or spots should be cleaned immediately.

  - Use water and as oft sponge or cloth for cleaning.

  - Do not use detergent or any abrasive material for panel cleaning.

  - Iso-propyl alcohol may be used to remove oil or grease stains.

  - Do not spray water on the panel if the panel glass is cracked or the back side is perforated.

  - Wipe water from module as soon as possible.

  - Use proper safety belts while cleaning modules atinclinedroofsetc.

  - The modules should not be cleaned when they are excessively hot. Early morning is particularly good time for module cleaning.

  - Check if there are any shade problems due to vegetation or new building. If there are, make arrangements for removing the vegetation or moving the panels to a shade-free place.

  - Ensure that the module terminal connections are not exposed while cleaning; this	 poses a risk of electric shock.

  - Never use panels for any unintended use, e. g. drying clothes, chips etc.

  - Ensure that monkeys or other animals donot damage the panels.

CABLES AND CONNECTION BOXES

- Check the connections for corrosion and tightness.

- Check the connection box to make sure that the wires are tight, and the water seals are not damaged.

- There should be no vermin inside the box.

- Check the cable insulating heath for cracks, breaks or burns. If the insulation is damaged, replace the wire

- If the wire is outside the building, use wire with weather-resistant insulation.

- Make sure that the wire is clamped properly and that it should not rub against any sharp edges or corners.

- If some wire needs to be changed, make sure it is of proper rating and type.

INVERTER

  - The inverter should be installed in a clean, dry, and ventilated area which is separated from, and not directly above, the battery bank.

  - Remove any excess dust in heat sinks and ventilations. This should only be done with a dry cloth or brush.

  - Check that vermin have not infested the inverter. Typical signs of this include

  - Spider webs on ventilation grills or wasps’ nests in heat sinks.

  - Check functionality, e.g. automatic disconnection upon loss of grid power supply, at least once a month.

  - Verify the state of DC/AC surge arrestors, cable connections, and circuit breakers.

SHUTTING DOWN THE SYSTEM

    - Disconnect system from all power sources in accordance with instructions for all other components used in the system.

    - Completely cover system modules with an opaque material to prevent electricity from being generated while disconnecting conductors.

    - To the extent possible, system shutdown will not be done during day time or peak generation.

INSPECTION AND MAINTENANCE SCHEDULE:

| Component | Activity | Description | Interval | By |
| --- | --- | --- | --- | --- |
| PV Module | Cleaning | Clean any bird droppings/ dark spots on module | Immediately | User/Technician |
|  | Cleaning | Clean PV moduleswith plain water or mild dishwashing detergent. Do not use brushes, any types of solvents, abrasives, or harsh detergents. | Fortnightly or as per the site conditions | User/Technician |

| Component | Activity | Description | Interval | By |
| --- | --- | --- | --- | --- |
| PV Array | Inspection | Check the PV modules and rack for any damage. | Annual | User/Technician |
|  |  | Note down location and serial number of damaged modules. |  |  |
|  | Inspection | Determine if any new objects, such as vegetation growth, are causing shading of the array and move them if possible. | Annual | User/Technician |
|  | Vermin Removal | Remove bird nests or Vermin fromarray and rack area. | Annual | User/Technician |
| Junction Boxes | Inspection | Inspect electrical boxes for corrosion or intrusion of water or insects. | Annual | Electrician |
|  |  | Seal boxes if required. |  |  |
|  |  | Check position of switches and breakers. |  |  |
|  |  | Check operation of all protection devices. |  |  |
| Wiring | Inspection | Inspect cabling for signs of cracks, defects, loose connections, overheating, arcing, short or open circuits, and ground faults. | Annual | Electrician |
| Inverter | Inspection | Observe | Monthly | Electrician |
| Component | Activity | Description | Interval | By |
|  |  | instantaneous operational indicators on the faceplate of the inverter to ensure that the amount of power being generated is typical of the conditions. Inspect Inverter housing or shelter for physical maintenance, if required. |  |  |

| Inverter | Service | Clean or replace any air filters. | As needed | Electrician |
| --- | --- | --- | --- | --- |
|  |  | Spot-check monitoring instruments |  |  |
| Transformer | Inspection | Inspect transformer oil level, temperature gauges, breather, silica gel, meter, connections etc. | Annual | Electrician |
|  | Inspection | Inspect gears, gear boxes, bearings as required. | Annual | Technician |
|  | Service | Lubricate tracker mounting bearings, gearbox as required. | Bi-annual | Technician |
| Plant | Monitoring | Daily Operation and Performance Monitoring | Daily | Site in charge |
| Inverter | Inspection | Observe instantaneous operational indicators on the faceplate of the inverter to ensure that the amount of power being generated is typical of the conditions. Inspect Inverter housing or shelter for physical maintenance, if required. | Monthly | Electrician |
| Inverter | Service | Clean or replace anyair filters. | As needed | Electrician |
| Instruments | Validation | Spot – check monitoring instruments (pyranometer etc.) with standard instruments to ensure that they are operational and within specifications. | Annual | PV Specialist |
| Transformer | Inspection | Inspect transformer oil level, temperature gauges, breather, silica gel, meter, connections etc. | Annual | Electrician |
| Tracker (if present) | Inspection | Inspect gears, gearboxes, bearings as required. | Annual | Technician |
|  | Service | Lubricate tracker mounting bearings, gearbox as required. | Bi-annual | Technician |
| Plant | Monitoring | Daily Operation and Performance Monitoring | Daily | Site in charge |
| Spare Parts | Management | Manage inventory ofspare parts. | As needed | Site in charge |
| Log Book | Documentation | Document all O&M activities in a workbook available to all service personnel | Continuous | Site in charge |

Annexure G

Operation and Maintenance Guidelines of Grid Connected PV Plants

- Periodic cleaning of solar modules, preferably once every fortnight.

- O&M of Solar Power Plant shall be compliant with grid requirements to achieve committed energy generation.

- Periodic checks of the Modules, PCUs and BoS shall be carried out as a part of routine preventive and breakdown maintenance.

- Immediate replacement of defective  Modules,  Invertors/PCUs  and  other equipment as and when required.

- Supply of all spares, consumables and fixtures as required. Such stock shall be maintained for  all associated equipments and materials as per manufacturer/ supplier’s recommendations.

- All the equipment testing instrument required for Testing, Commissioning and O&M for the healthy operation of the Plant shall be maintained by the Bidder. The  testing  equipments must be calibrated once every 2 years from NABL accredited labs and the certificate of calibration must be kept for reference as required.

- If negligence/mal-operation on part of the Bidder's operator results in failure of equipment, such equipment should be repaired/replaced by the Bidder free of cost.

- If any jobs covered in O&M Scope as per RFS are not carried out by the contractor/Bidders  during the O&M period, the Engineer-In-Charge shall take appropriate action as deemed fit.

- DISCOMs reserves the right to make surprise checks/inspection visits at its own or through authorized representative to verify the O&M activities being carried out by the Bidder. Failure to adhere to above guidelines will result in penal action including debarring from participation in next tender

ANNEXURE H

Quality Certification, Standards and Testing for Grid-connected Rooftop Solar PV Systems/Power Plants

Quality certification and standards for grid-connected rooftop solar PV system sare essential for the successful mass-scale implementation of this technology. It is also imperative to put in place an efficient and rigorous monitoring mechanism, adherence to these standards. Hence, all components of grid-connected rooftop solar PV system/ plant must conform to the relevant standards and certifications given below:

| Solar PV Modules/Panels |  |
| --- | --- |
| IEC 61215/IS 14286 | Design Qualification and Type Approval for Crystalline Silicon Terrestrial Photovoltaic (PV) Modules |
| IEC 61701 | Salt Mist Corrosion Testing of Photovoltaic (PV) Modules |
| IEC 61853-Part 1/ IS 16170:Part 1 | Photovoltaic (PV) module performance testing and energy rating: Irradiance and temperature performance measurements, and power rating |
| IEC 62716 | Photovoltaic (PV) Modules–Ammonia(NH3) Corrosion Testing (As per the site condition like dairies, toilets) |
| IEC 61730-1,2 | Photovoltaic (PV) ModuleSafetyQualification–Part1: Requirements for Construction,Part2:Requirementsfor Testing including “Fire Test MST 23” |
| IEC 62804 | Photovoltaic (PV) modules-Test methods for the detection of potential-induced degradation. IEC TS62804-1:Part1: Crystalline silicon (mandatory for applications where the system voltage is > 600VDC and advisory for installations where the system voltage is <600 VDC) |
| IEC 62759-1 | Photovoltaic (PV) modules–Transportation testing, Part1: Transportation and shipping of module package units |
| Solar PV Inverters |  |
| IEC 62109-1,IEC 62109-2 | Safety of power converters for use in photovoltaic power systems– Part 1:General requirements, and Safety of power converters for use in photovoltaic power systems Part 2:Particular requirements for inverters. Safety compliance (Protection degree IP 65 for outdoor mounting, IP 54for indoor mounting) |
| IEC/IS 61683 (as applicable) | Photovoltaic Systems – Power conditioners: Procedure for Measuring Efficiency (10%, 25% , 50% , 75% & 90-100% Loading Conditions) |

| BS EN 50530 (as applicable) | Overall efficiency of grid-connected photovoltaic inverters: This European Standard provides a procedure for the measurement of the accuracy of the maximum power point tracking (MPPT) of inverters, which are used in grid- connected photovoltaic systems. In that case the inverter energizes a low voltage grid of stable AC voltage and constant frequency. Both the static and dynamic MPPT efficiency is considered. |
| --- | --- |
| IEC 62116/ UL 1741/ IEEE 1547 (as applicable) | Utility-interconnected Photovoltaic Inverters - Test Procedure of Islanding Prevention Measures |
| IEC 60255-27 | Measuring relays and protection equipment – Part 27: Product safety requirements |
| IEC 60068-2 (1, 2, 14, 27, 30 & 64) | Environmental Testing of PV System – Power Conditioners and Inverters - IEC 60068-2-1: Environmental testing - Part 2-1: Tests - Test A: Cold - IEC 60068-2-2: Environmental testing - Part 2-2: Tests - Test B: Dry heat - IEC 60068-2-14: Environmental testing - Part 2-14: Tests - Test N: Change of temperature - IEC 60068-2-27: Environmental testing - Part 2-27: Tests - Test Ea and guidance: Shock - IEC 60068-2-30: Environmental testing - Part 2-30: Tests - Test Db: Damp heat, cyclic (12 h + 12 h cycle) - IEC 60068-2-64: Environmental testing - Part 2-64: Tests - Test Fh: Vibration, broadband random and guidance |
| IEC 61000 – 2,3,5 (as applicable) | Electromagnetic Interference (EMI) and Electromagnetic Compatibility (EMC) testing of PV Inverters |
| Fuse |  |
| IS/IEC 60947 (Part 1, 2 & 3), EN 50521 | General safety requirements for connectors, switches, circuit breakers (AC/DC): - Low-voltage Switchgear and Control-gear, Part 1: General rules - Low-Voltage Switchgear and Control-gear, Part 2: Circuit Breakers - Low-voltage switchgear and Control-gear, Part 3: Switches, disconnectors, switch-disconnectors and fuse-combination units - EN 50521: Connectors for photovoltaic systems – Safety requirements and tests |
| IEC 60269-6 | Low-voltage fuses - Part 6: Supplementary requirements for fuse-links for the protection of solar photovoltaic energy systems |
| SurgeArrestors |  |
| IEC 62305-4 | Lightening Protection Standard, CEA safety regulations |
| IEC 60364-5-53/ IS 15086-5(SPD) | Electrical installations of buildings- Part 5-53:Selectionand erection of electrical equipment- Isolation, switching and control |

| IEC 61643- 11:2011 | Low-voltage surge protective devices- Part 11:Surge protective devices connected to low-voltage power systems- |
| --- | --- |
| Cables |  |
| IEC 60227/IS694, IEC 60502/IS1554 (Part 1&2)/ IEC69947 | General test and measuring method for PVC (Polyvinyl chloride) insulated cables (for working voltages upto and including1100V,andUV resistant for outdoor installation) |
| BS EN 50618 | Electric cables for photovoltaic systems (BT(DE/NOT)258), mainly for DC Cables |
| Earthing/Lightning |  |
| IEC 62561Series (Chemical earthing) | IEC 62561-1: Lightning protection system components (LPSC)- Part 1: Requirements for connection components IEC 62561-2: Lightning protection system components(LPSC)- Part 2: Requirements for conductors and earth electrodes IEC 62561-7: Lightning protection system components (LPSC)- Part 7: Requirements for earthing enhancing compounds |
| Junction Boxes |  |
| IEC 60529 | Junction boxes and solar panel terminal boxes shall be of the thermo-plastic type with IP65protectionfor outdoor use, and IP 54protectionfor indoor use |
| Energy Meter |  |
| IS 16444 or as specified by the DISCOMs | A.C.Static direct connected watt-hour Smart Meter Class1 and2— Specification(with Import &Export energy measurements) |
| Solar PV Roof Mounting Structure |  |
| IS 2062/IS4759 | Material for the structure mounting |

Note: Equivalent standards may be used for different system components of the plants.