| Tender Document For Design, Supply, Installation & Commissioning of Solar RTPV Grid connected power plants of100 KWp on the Roof-top of Bagalkot District Central Co-operative Bank Ltd, Head office,Navanagar 24th Sector,Bagalkot – 587 103 with Net Metering& Annual Maintenance contract for a period of five years. |  |
| --- | --- |
| Bagalkot DCC Bank invites tender forDesign, Supply, Installation &Commissioning of Solar RTPV Grid connected power plants of 100 KWp |  |

- The work of: Design, Supply, Installation & Commissioning of Solar RTPV Grid connected power plants of 100 KWp.

- EMD AMOUNT: Rs. 1,00,000.00

Earnest Money Deposit/ Bid security

The supplier/contractor can pay the Earnest Money Deposit (EMD) in the e-Procurement portal using any of the following payment modes

- Credit Card

- Direct Debit

- Net Banking

- National Electronic Fund Transfer (NEFT)

- Over the Counter (OTC)

- TIME OF PROJECT: 180 days.

4 . The Bidder should go through the Tender Document and submit the response commercial/Technical through e-   procurement portal online after downloading the tender

5. Documents may be downloaded from Government of Karnataka e-Procurement website https://eproc.karnataka.gov.in/eportal/index.seam under login for Bidder:

Tender Number:							           Dated: 12-08-2021

| 01 | Last date & Time for Tender Queries/Clarification | 27/08/2021 Up to 4.00 PM |
| --- | --- | --- |
| 02 | Last date & Time for Receipt of Tender | 02/09/2021 Up to 4.00 PM |
| 03 | Date & Time for opening of Technical Bid | 04/09/2021 Up to 11.00 AM |
| 04 | Date & Time for opening of Financial Bid | 08/09/2021 Up to 11.00 AM |

Sd-

Chief Executive Officer

# About US.

The Bagalkot District is carved out of the earlier Bijapur District and came in to being on 15th August 1997. The district has two revenue sub-division viz Bagalkot and Jamakhandi, six tehsils viz Bagalkot, Badami, Hunagund, Jamakhandi, Mudhol, Bilagi, and consisting of 223 revenue villages.

There are 213 branches of different banks in the district, which include 89 branches of commercial banks, 60 ranches of RRBBs, 21 Branches of private sector banks, 36 branches of DCCBs and PCARD Banks, There is one branch of KSFC.

The DCC bank Ltd Bagalkot is the result of the bifurcation of the Bijapur DCC Bank and has started functioning from 01.03.2003. The Reserve Bank of India has granted banking license on 15.12.2011

At present the Bank has 44 branches, 3 extension counters and Head office is
catering to the financial needs of 262 PACS and many other co-operatives affiliated to the Bank.

The bank presently has 28 onsite ATMs to cater to customers. Bank has mobile banking facility through state of art ATM van to provide banking facility to rural areas.

Technical Details

- SCOPE OF WORK:

  - Design, Supply, Installation, Metering, Testing and Commissioning of Solar RTPV grid connected plant as per the technical specifications notified by MNRE/GoK/KERC and any other applicable laws including but not limited to regulations notified by Karnataka Electricity Regulatory Commission (KERC).

  - Transportation of materials to Site, unloading at site, handling, storage, associated civil works, services, permits (material related), insurance at all stages, construction, erection, installation, testing (pre-grid and post grid), commissioning, performance testing, trial run, training to BDCC nominated representatives.

  - Execution of a Power Purchase Agreement (PPA) in the Commission approved standard format on net metering basis between BDCC&HESCOM

  - Performance testing of the complete system.

  - Submission of Work Completion Report along with drawings and test reports of all the equipment’s.

  - Risk liability of all personnel associated with installation, testing and commissioning of the project and AMC period of 5 yrs.

  - Training on the various aspects of maintenance of the system after commissioning for the consumer.

  - A technical Person should be there to supervise the SRTPV plant installation.

  - Entering into Annual Maintenance Contract (AMC) with consumers for 5 years.

- TECHNICAL SPECIFICATION:

  - STANDARDS

| Applicable BIS /Equivalent IEC Standards / Applicable MNRE Specifications |  |  |  |
| --- | --- | --- | --- |
| Standard Description |  |  | Standard Number |
| 1 | Crystalline Silicon Terrestrial PV modules mono | IEC 61215/ IS14286 |  |
| 2 | Solar PV module safety qualification requirements | IEC 61730 (P1 – P2) |  |
| 4 | Cables | IEC 60227 / IS 694 IEC 60502 / IS 1554 (Part I & II) |  |
| 5 | Earthing | IS 3043: 1986 |  |
| 6 | Switches/ Circuit Breakers/ Connectors | IEC 60947 Part I,II, III / IS 60947 Part I,II, III / EN 50521 |  |
| 7 | Junction Boxes/ Enclosures for Charge Controllers/ Luminaries | IP 65 (for outdoor)/ IP 21 (for indoor) As per IEC 529 |  |

  - SOLAR PV MODULES

| Type | Crystalline silicon –Mono |
| --- | --- |
| Module Efficiency | >= 20% |
| Standard | UL 1703 certified, Electroluminescence tested to ensure microcrack free panels, PID resistant |
| Power warranty | 25 years warranty on solar panel & 5 years other material warranty |
| Performance Warranty | Should not be less than 90% of designed nominal power at the end of 10 years and 80% of designed nominal power at the end of 25 years. |
| Module frame | Anodized aluminum, non-corrosive and electrolytically compatible mounting structure. |
| Module minimum rated power | The nominal power of a single PV module shall be >=385Wp. |
| Power output rating | To be given for standard test conditions (STC). I-V curve of the sample module should be submitted. |

2.3 MOUNTING STRUCTURE

The solar PV modules shall be mounted on fixed metallic structures of adequate strength and appropriate design, which can withstand the load of the modules and high wind velocities up to 150 km per hour.

- The module mounting structure will be designed in such a way that it will occupy minimum space without forfeiting the output from Solar generating power plant & shall be designed to allow easy replacement of any module.

- Bidder has to design foundation (RCC and PCC) and structure considering the wind loads and structural load bearing capacity of the building. The System integrator must ensure proper water proofing in case of any modifications to the roof.

- Detailed specifications for the mounting structure are given below:

| Wind velocity withstanding capacity | 150 km / hour |
| --- | --- |
| Structure material | Structural materials shall be corrosion resistant and electrolytically compatible with the materials used in the module frame, its fasteners, nuts and bolts. |
| Bolts, nuts, fasteners, panel mounting clamps | Stainless steel SS304 |
| Mounting arrangement for flat roofs | With Removable concrete ballast made of Pre-fabricated PCC -1:1.5:3, M20 |
| Installation | The structures shall be designed for simple mechanical on-site installation |
| Minimum distance between roof edge and mounting structure (Horizontal Clearance) | >= 0.60 m |
| Minimum clearance between lowest part of panel and mounting structure (Vertical Clearance) | Shall not be less than 100mm |
| Access for panel cleaning and maintenance | All solar panels must be accessible from the top for cleaning and from the bottom for access to the junction box |
| Panel tilt angle | North – south orientation with a fixed tilt angle 10degree(south facing) |

2.4ARRAY JUNCTION BOX

The array junction boxes are free of dust, vermin, and waterproof and made of Thermo Plastic. The terminals will be connected to copper bus-bar arrangement of proper sizes made of tin copper flats. The array junction boxes will have suitable cable entry points fitted with cable glands of appropriate sizes for both incoming and outgoing cables.

| Technical Specification – Junction Boxes |  |
| --- | --- |
| Material | Dust, Vermin & Water proof Thermoplastic |
| Hardware SS 304 | Cable Gland Thermoplastic |
| Protection | IP 65 enclosures with transparent covers with Surge Protection Device (SPD) class-I/II, DC Fuse with holder and string disconnector. |

  - SURGE PROTECTION DEVICE (SPD):

Internal surge protection shall consist of three MOV/GDT (glass discharge tube) type arrestors connected from +ve and –ve terminals to earth (via Y arrangement) for higher withstand of the continuous PV-DC voltage during earth fault condition. SPD shall have safe disconnection and short circuit interruption arrangements through integrated DC inbuilt bypass fuse (parallel) which should get tripped during failure mode of MOV, extinguishing DC arc safely in order to protect the installation against fire hazards.

Nominal discharge current(In)shall be minimum of 10kA with max. discharge current (Imax) of 20kA with discharge time of 8/20 micro seconds.

- A surge protection device in each sub-array line shall be provided to prevent the high current transients from entering into the DC bus.

- It must be with DC disconnect switch and DC fuses positive side shall have a voltage rating of 1000V DC, current rating as required.

  - DC DISTRIBUTION BOX

A DC distribution box shall be mounted close to the solar grid inverter. The DC distribution box shall be of thermo plastic IP65 DIN rail mounting type and shall comprise the following components and cable terminations:

- 2 pole DC circuit breaker

- DC surge protection devise (SPD) class 2 as per IEC 60364-5-53.

- Cable termination glands for DC cables from DC combiner box and grid inverter.

As an alternative to the DC circuit breaker, a DC isolator may be used inside the DC Distribution Box or in a separate external thermoplastic IP 65 enclosure adjacent to the DC Distribution Box. If a DC isolator is used instead of a DC circuit breaker, a DC fuse shall be installed inside the DC Distribution Box to protect the DC cable that runs from the DC Distribution Box to the Solar Grid Inverter.

  - AC DISTRIBUTION BOX

An AC distribution box shall be mounted close to the solar grid inverter. The AC distribution box shall be of wall / rail mounting type and shall comprise of following components:

  - 2 pole / 4 pole AC circuit breaker.

  - AC surge protection device (SPD), class 2 as per IEC 60364-5-53.

  - Suitable cable termination glands for cable from inverter and electrical distribution board.

A manual disconnect switch beside automatic disconnection to grid would have to be provided at utility end to isolate the grid connection by the utility personal to carry out any maintenance. This switch shall be locked by the utility personal.

  - DC AND AC CABLES:

- All Cables shall confirm to relevant IS/ IEC standards.

- For the DC cabling, XLPE insulated and PVC sheathed, UV stabilized single core flexible copper cables shall be used. Multi-core cables shall not be used.

- For the AC cabling, PVC or XLPE insulated and PVC sheathed single or multi-core flexible copper cables shall be used. Aluminum cables also can be used(Aluminium shall be used for AC Cable) but shall be of properly designed minimum cross section area of the conductor. Outdoor AC cables shall have a UV-stabilized outer sheath.

- The total voltage drop on the cable segments from the solar PV modules to the solar grid inverter shall not exceed 2.0%.

- The total voltage drop on the cable segments from the solar grid inverter to the building distribution board shall not exceed 2.0%

- The DC cables from the SPV module array shall run through a UV stabilized PVC conduit pipe of adequate diameter with a minimum thickness of 1.5mm.

- Cables and wires used for the interconnection of solar PV modules shall be provided with solar PV connectors and couplers.

- All cables and conduit pipes shall be clamped to the rooftop/ walls/parapet with thermo-plastic clamps at intervals not exceeding 50 cm.

- The minimum DC cable size shall be 4.0 mm2 copper. The minimum AC cable size shall be 4.0 mm2 copper. In three phase systems, the size of the neutral wire size shall be equal to the size of the phase wires.

- Cables that have to pass through walls or ceilings shall be taken through a PVC pipe sleeve.

- Cable conductors shall be terminated with tinned copper end-ferrules to prevent fraying and breaking of individual wire strands. The termination of the DC and AC cables at the Solar Grid Inverter shall be done as per instructions of the inverter manufacturer, which in most cases will include the use of special connectors.

Only copper cables of appropriate size and of reputed-make shall have to be used. However, aluminum cables can be used on A.C side.

- All connections should be properly terminated, soldered and/or sealed from outdoor and indoor elements. Relevant codes and operating manuals must be followed. Extensive wiring and terminations (connection points) for all PV components is needed along with electrical connection to lighting loads.

- Only terminal cable joints will be accepted. No cable joint to join two cable ends shall be accepted. All cable/wires shall be marked with good quality letter and number ferrules of proper sizes so that the cables can be identified easily.

  - EARTHING PROTECTION

A minimum of two separate dedicated and interconnected earth electrodes must be used for equipment earthing both on DC side and AC side.

- Earthing shall be done in accordance IS 3043-1986, provided that earthing conductors shall have a minimum size of 6.0 mm2 copper wire or 10 mm2 Aluminum wire or 3mm X 70 mm hot dip galvanized iron flat. Unprotect Aluminum or copper-clad Aluminum conductors shall not be used for final underground connections to earth electrodes.

- The earth electrodes shall have a pre-cast concrete enclosure with a removal lid for inspection and maintenance. The entire earthing system shall comprise non-corrosive components.

  - CAUTION SIGNS

In addition to the standard caution and danger boards or labels as per Indian Electricity Rules, the AC distribution box near the solar grid inverter and the building distribution board to which the AC output of the solar PV system is connected shall be provided with a noncorrosive caution label with the following text:

WARNING –DUAL POWER SOURCE

SECOND SOURCE IS SOLAR SYSTEM

The size of the caution label shall be 105mm (width) x 20mm (height) with white letters on a red background.

2.11 GRID INVERTER AND BI-DIRECTIONAL METER:

Only HESCOMempaneled grid tied inverters and bi-directional meters shall be used

  - METERING SCHEME:

The bi-directional (import kWh and export kWh) meter shall be fixed at the point of grid connectivity (the “Solar Service Connection Meter”) for the purpose of net-metering as per SLD enclosed as Annexure:

The existing meter shall be rewired to record total solar generation.

Both bi-directional and solar generation side meter shall be in the same vicinity.

  - PLANT MONITORING

  - A data logging system for plant monitoring shall be provided.

# Eligibility Criteria and other conditions:

- Bidder should have been an established firm with at least 2years’ experience in solar PV rooftop power plant engineering, design, procurement, testing & commissioning & should have associated with OEM as Channel Partners for the last 2 years

- The panels supplied should have been a manufacturer of modules for at least 3 years and should have manufactured and supplied the solar PV modules of cumulative capacity of 1 MWp in any one financial year

- The bidder/OEM should have designed, supplied, erected and commissioned SPV based grid connected rooftop-based power plants as below:

- One single plant of 100 kWp or above

- Cumulative capacity of 1 MWp or above

- Minimum of 100kW of grid connected roof top installations in any district of Karnataka by OEM or through its Channel partners

- The reference plant of 100 kWp or above capacity must have been in successful operation for at least six months as on date of techno-commercial bid opening.

- Bidder must provide authorization from OEM for product and support. In case bidder fails to support, OEM must support the project.

- The turnover of the OEM, in the preceding Two (2) financial years as on the date of Techno Commercial bid opening, shall not be less than Rs.3 Crores.

- Before participating for tender bid, you can visit site location and see the availability of site area.

- The bidder’s company/OEM firm must have established quality assurance systems andorganization in line with the requirements under ISO 9001:2015.

- The OEM must have a valid BIS certificate at the time of bid submission.

- Bidder shall have a Centralised Customer care and technical team to handle after Sales service.

- OEM should have enlisted under approved list of manufacturers for Poly and Mono modules published by MNRE

- Bidder/OEM should have supplied rooftop-based power plants of value of minimum   	35 lakh in last two years.

- Bidder must quote all the items for this project from a single OEM.

- Bidder, if not OEM, should have associated with OEM as Channel Partners for the last 2 years. In that case OEM should meet the eligibility criteria as stipulated by the tenderer. The bidder should obtain all the required documents from the OEM for participating in the tender on behalf of OEM besides obtaining authorisation from OEM for participating in the tender.

- THE RIGHT TO ACCEPT THE TENDER IN FULL OR IN PART AND THE TENDERER SHALL HAVE NO CLAIM FOR REVISION OF RATES/OTHER CONDTIONS IF HIS TENDER IS ACCEPTED IN PART.

- The Bank does not bind itself to accept the lowest or any tender and reserves to itself the right of accepting the whole or any part of the tender and the tenderer shall be bound to perform the same at the rate quoted. Bank reserves the right to select the brand and model of item quoted based on performance and support criteria.

- On acceptance of the tender, the name of the accredited representative (s) of the contractor who would be responsible for taking instructions from the Bank shall be communicated to the Bank.

- In case of other un- successful tenderers, the EMD shall be returned treating it individually. The Bank reserves the right to accept or reject any of the offers, without assigning any reason and no dispute or negotiation will be entertained in this regard. The Bank's decision will be final in the matter.

- No interest shall be allowed on the Earnest Money. Tenders without Earnest Money shall be liable for rejection.

- AMC shall be for a period of minimum 5 years and renewed on annual basis as per performance.

- PV Modules: 25 years warranty & 5 year product warranty.

- Inverters: 5 year warranty against manufacturing defects.

- All other equipment: 5year warranty against manufacturing defects.

- Proper and adequate training must be provided to personals deputed by the bank.

- Agreement must be signed with the bank for at least 5 years.

- Vendor should make sign and seal in all pages with remark as complied.

- If any deviation, Vendor should submit related documents.

- Price bid of only technically qualified bidders will be opened later.

- The substantial responsiveness will be in terms of the Karnataka Transparency in Public Procurement Act & incomplete bids are liable to be rejected.

- If the lowest bidder does not agree to withdraw the deviations, Bagalkot DCC bank Ltd reserves the right to negotiate with the next lowest bidder.

- The substantial responsiveness will be in terms of the Karnataka Transparency in Public Procurement Act & incomplete bids are liable to be rejected.

- Bank Ltd reserves the right to request for additional information and also reserves the right to reject the proposal of any bidders, if in its opinion, the qualification and other data is incomplete.

- Documents furnished will be scrutinized to determine the bidders meeting the qualification criteria. The price bid of only those Bidders who are qualified as per qualification criteria would be opened.

- Bank reserves the right to cancel or withdraw or modify the bid without assigning any reason for such decision. Such decision will not incur any liability whatsoever on the part of Bagalkot DCC bank Ltd. consequently.

- The Bid must contain the name, designation and place of business of the person or persons submitting the bid and must be signed.

- Bids by a Company / Firms shall be signed by the authorized persons of the bidding business entity indicating their proper legal name.

- The Bidder’s name stated in the proposal shall be the exact legal name of the firm.

- Erasures or other changes in the bid shall be initialled by the person signing the bid.

- Time Schedule: Work shall be completed with (180 days) of placing of work order.

- Bidder must understand the entire setup and have necessary technical expertise for implementation of the solution.

.

- Payment:

- 70% of the value will be released on receipt and acceptance of all the items in good condition at site.

- Balance 25% will be released on successful installation and commissioning and submission of bank guarantee.

- 1% after completion of 1st year AMC from the date of successful installation.

- 1% after completion of 2nd year AMC from the date of successful installation.

- 1% after completion of 3rd year AMC from the date of successful installation.

- 1% after completion of 4th year AMC from the date of successful installation.

- 1% after completion of 5th year AMC from the date of successful installation..

- Bids not conforming to the above requirements are liable to be rejected.