## Pre Bid Queries
Tender for Design, Engineering, Supply, Construction, Erection, Testing, commissioning and O&M of 5 MW (AC) Grid connected Saffron based Argo-Solar PV Project at Pampore, Pulwama, JK, India
Tender No : SECI/C&P/PMC/11/0002/2021-22
Sl. No. | Tender Section | Page No. | Clause No | Description as per Tender Document | Queries | Category (Finance/Technical/Contractual) | Clarifications
1 | Project particulars | 6 |  | Performance parameter Performance Ratio at Plant End 82% Capacity Utilization Factor at Substation End 23% | 82% PR is very high for 60%overloading,. Bidder request to revise | Technical | Minimum DC capacity specified in the tender document is 6.5 MWp, i.e. 30% overloading. The terms and conditions of the tender document shall prevail.
2 | 4 Procurement & Supply | 9 | 4.9 | Inverter transformers of appropriate rating (2 × 2.5 MVA). | Bidder request to accept 5 MVA inverter also as per current market availability | Technical | Kindly refer Amendment-1.
3 | 4 Procurement & Supply | 10 | 4.1 | 33 kV Indoor Gas Insulated Switchgear (GIS) Panels including Vacuum Circuit Breakers, Current Transformers, Voltage Transformers, Relays and other accessories for complete protection. Outgoing feeder of GIS panel shall be rated for 10 MW. | Bidder request to Accept for 33kV Air insulated switchgear (outdoor) | Technical | GIS has been proposed in the tender document considering limited space availability. The terms and conditions of the tender document shall prevail.
4 | 4 Procurement & Supply | 34 | 4.3 | 4.3 Technical Requirements (table) Degree of protection Central Inverter – IP 20 (Indoor), String Inverter – IP 65 | Bidder request to accept for IP54 for central inverter as per the latest market availability | Technical | Considering limited space availability, outdoor central inverters are not allowed. Central inverter shall be indoor only with minimum degree of protection of IP 20. The terms and conditions of the tender document shall prevail.
5 | 5 Inverter Transformer and Auxiliary Transformer | 38 | 5.2 | 5.2 Technical Requirements, Winding (Inverter transformer: As per system design requirement | Bidder understands the Winding conductor of inverter duty transformer can be electrolytic grade Copper/Aluminum. Please confirm. | Technical | Transformer winding conductor can be made of electrolytic grade Copper or electrolytic grade Aluminum.
6 | 18 CCTV Camera | 76 | 18 | CCTV camera | Bidder request to provide the Detailed specification of CCTV cameras at each strategic location | Technical | The Bidder shall fulfill the specifications provided in Clause 18 of Part-B of Section-VII(B). Detailed specifications will be finalized during detailed engineering. The terms and conditions of the tender document shall prevail.
7 | Autocad drawing | - | - | - | Bidder request to provide the heights of : Exisitng structure not to be disturbed" as mentioned in Autocad drawing | Technical | Taken Into account. Kindly see Amendment-1
8 | Autocad drawing | - | - | - | Bidder request to provide the heights of : HT tower and Water tank" as mentioned in Autocad drawing | Technical | Taken Into account. Kindly see Amendment-1
9 | Autocad drawing | - | - | - | Bidder request to provide the GA and SLD of : Existing structure to be used for MCR" as mentioned in Autocad drawing | Technical | Plan of existing Control Room is provided in Annexure-F (Tender Drawings) of Section-VII. Existing SLD of Control Room is not relevant to the proposed project.
10 | General | - | - | - | Bidder request to provide the typical SLD of the Solar plant. | Technical | Typical power evacuation scheme is attached as part of Annexure-F (Tender Drawings). Kindly refer Amendment-1.
11 | General | - | - | - | Bidder request to provide theTopo and contour report for Land | Technical | Data not available.
12 | SCHEDULE OF RATES [SOR-1] in excel (Section-VIII_Format for SOR | Work sheet-1 | 11 | Transmission line approx 4.4 Kms (3.2 Kms overhead & 1.2 Kms underground). | As per the site survey 33kV OH line will be connected to the exiting transmission line as LILO. Please clarify | Technical | Kindly refer Amendment-1.
13 | Technical | - | - |  | What is the minimum height required from FGL to bottom edge of the module for MMS | Technical | Kindly refer Clause 13.32 of Part-C of Section-VII(B).
14 | A Design Philosophy 4 Design Conditions | 24 | 4.1 | Minimum inter-row spacing shall be 2m. Leaving 500 mm width in front and back of the Module Mounting Structure (MMS) for maintenance purpose, remaining area in between MMS shall be reserved for agricultural activities | Please clarify providing the sample array layout for more understanding | Technical | Reference drawing (Area Utilization) is attached as part of Annexure-F (Tender Drawings). Kindly refer Amendment-1.
15 | General | - | - | - | What is the distance between the power evacuation take off point to MCR location | Technical | Kindly refer Amendment-1.
16 | Section VII | 74/101 | 6.1 | There shall be no peripheral road. However, about 2.5m wide corridor compacted to a depth of 300mm shall be left along inside of the plant boundary suitably maintained clean of any vegetation and shall be provided with adequate illumination for movement of security personnel. | In Spec Stating No Peripheral Road and Asking Compacted to a depth of 300mm along boundary pls clarify the same. | Technical | Peripheral road need not to be constructed. However, 2.5m wide peripheral corridor shall be provided as per the given specifications. The terms and conditions of the tender document shall prevail.
17 | General | - | - | Cement & Steel | No Manufacture Makes of Cement and Steel Indicated , Pls confirm the same if any reputed brands required. | Technical | Manufacturer list has not been provided for Cement and Steel. Manufacturer who comply with the tender specifications and applicable Indian standards/codes can be used.
18 | Section VII | 76/101 | 8 | The boundary wall shall comprise of pre-stressed precast RCC wall panels (min. 75mm thick) and columns (min. 200 mm x 200 mm) of M30 grade The founding depth (below NGL) for the precast column shall be min. 600 mm and the column shall be embedded in PCC (1:2:4) block of 600 mm x 600 mm. | Is Bidder is allowed to Propose Precast Boundary Wall with 150 X 150 mm the column post and 50 mm the Panels pls clarify the same. With 300 Dia Pile. | Technical | Boundary wall is removed from the scope of EPC Contractor. Kindly refer Amendment-1.
19 | IFB | 10 | 6(iii) | Third Contract (O&M Part): For providing Comprehensive operation & maintenance of the Solar PV plant for 15 (Fifteen) years from the date of Operational Acceptance, as detailed in technical specification including supply and storage of all spare parts, consumables, repairs/ replacement of any defective equipment etc. | Request to please clarify on the O&M Time period for the Solar-PV plant | Contractual | Typo is corrected in Ammendment-1. O&M period will be of 10 years as mentioned in the tender document
20 | GCC | 39 | 43.3.2 e | All the required approvals and NOC’s as required, are submitted | as the Land is not under Defense Zone, we kindly request to remove the Defense NOC from the Bidders scope-if any. | Contractual | The terms and conditions of the tender document shall prevail.
21 | SOW | 12 | 7.1 | Pollution control board clearance, if required | as the Pollution is not a concern point for the Solar PV plant- Request to remove the Pollution control board Clerance in Bidders scope | Contractual | The terms and conditions of the tender document shall prevail.
22 | BDS | 3 | 6 | The bid validity period shall be 180 (One Hundred and Eighty Days) from the date of opening of Techno-Commercial Bid (Envelope-I). | Request to change the Bid Validity date from 180 days to 120 days from the date of opening of techno-Commercial Bid. | Contractual | The terms and conditions of the tender document shall prevail.
23 | SOW | 3 | 1 | Available land Area | as per the site survey the provided land of 22.5 acers is not sufficient for 6.5MWp as per our understanding, Kindly request to please clarify on the land portion. | Technical | The terms and conditions of the tender document shall prevail.
24 | General | - | - | Hydrology Report | Request to please share the Hydrology report & water source. | Technical | Data not available.
25 | Section VIII | 10 | 4.1 | 33 kV Indoor Gas Insulated Switchgear (GIS) Panels including Vacuum Circuit Breakers, Current Transformers, Voltage Transformers, Relays and other accessories for complete protection. Outgoing feeder of GIS panel shall be rated for 10 MW. | As per our understanding, 33 KV power cable from transformer should go directly to Control room building Indoor GIS Kindly confirm the number of bays to be considered in GIS. Like no of incoming bays and outgoing bays with rating | Technical | Typical power evacuation scheme is attached as part of Annexure-F (Tender Drawings). And, the referred clause is also amended. Kindly refer Amendment-1.
26 | General | General | - | Space constrain | Only 22.5 Acre is available including all the shadow and common access roads General : Plant area is very tight, In event if we conclude the land space is insufficient during detailed shadow analysis of all surrounding structures (Shadow analysis) to meet 23% CUF. Can we consider sheet roof for installation of shortfall capacity | Technical | The terms and conditions of the tender document shall prevail.
27 | Section VIII | 112 | 23 | Supplier Qualification: The Robotic Cleaning System Supplier/Sub-Contractor must have experience of having successfully completed Design, Engineering, Installation, Testing and Commissioning of Robotic Module Cleaning systems for at least 2 Solar PV Projects of minimum capacity of 5 MW in the last 5 years. Such systems must have been in satisfactory operation for at least 12 months from the date of Commissioning | Suppliers are limited. The robotic system life is not guaranteed for longer period of operation also warranty is limited two years. we request SECI to consider only manual cleaning since it is more economical and practical also reliability is not there. If SECI insists kindly accept the following 1. Warranty is limited to two years only for entire robotic cleaning system and after two years repair/service charges on chartable basis 2. Penalty should be applicable after 10 days from the date of intimation from SECI since vendor has to rectify the system 3. No penalty for robotic cleaning system after 2 years | Technical | The terms and conditions of the tender document shall prevail.
28 | Section VIII | 112 | 23 | The Robotic Cleaning system shall be self-powered, with battery backup (no external supply). The battery shall be compliant with IEC 62133: Secondary cells and batteries containing alkaline or other non-acid electrolytes - Safety requirements for portable sealed secondary cells, and for batteries made from them, for use in portable applications. | It has to powered from AC auxiliary supply otherwise additional modules to be considered for battery charging and operation. Battery operation in outdoor is not recommended in these location since life and reliability is not guaranteed we request SECI not to consider Robotic system. If SECI insists kindly accept the following 1. Warranty is limited to two years only for entire robotic cleaning system and after two years repair/service charges on chargeable basis 2. Penalty should be applicable after 10 days from the date of intimation from SECI since vendor has to rectify the system 3. No penalty for robotic cleaning system after 2 years | Technical | The terms and conditions of the tender document shall prevail.
29 | SCC | 154 | 10 | The value of the Contract Performance Security shall be 4% (Four percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). | As per Ministry of finance OM dated 30.12.2021 , Kindly consider 3% PBG Kindly accepts initial 3% PBG for 12 + 3 months. Same shall be extended for year on year basis till completion of contract | Finance | Kindly refer Amendment-1.
30 | SECTION - VI | 214 | 2 (b) | b) Contractor agrees to submit required evidences for conformance to IEC/ISO:15408 for identified network-based systems such as routers, firewalls, SIEMs etc. | Need to submit this IEC/ISO: 15408 along with the bid document or after the issue of work order. | Technical | Needs to be submitted along with the bid document.
31 | Annexure-D | 228 | D | CUF given in the document is 23 % | Kindly lower the CUF value. | Technical | The terms and conditions of the tender document shall prevail.
32 | Section III | 70 | 1.4.5 | The Bid Securing Declaration & Performance Security (In case of award) of a JV/Consortium shall be in the name of the JV/Consortium that submits the Bid. If the JV/Consortium has not been legally constituted into a legally enforceable JV/Consortium at the time of bidding, the Bid Securing Declaration shall be in the names of all the members of the JV/Consortium & not in the name of “only lead bidder”. The Bid Securing Declaration shall be executed in the names of all the members of the JV/Consortium. | Is it mandatory to both member name in Bank Guarantee format for EMD. | Contractual | Yes. Pl refer section "Annexure to BDS" for clarity on the JV/consortium.
33 | Section-VII | 94 | 23 | 1. The PV Module Cleaning system shall be dry, Robotic type with microfiber-based brushes. 2. Supplier Qualification: The Robotic Cleaning System Supplier/Sub-Contractor must have experience of having successfully completed Design, Engineering, Installation, Testing and Commissioning of Robotic Module Cleaning systems for at least 2 Solar PV Projects of minimum capacity of 5 MW in the last 5 years. Such systems must have been in satisfactory operation for at least 12 months from the date of Commissioning. The Contractor shall submit supporting documents as credentials, including Purchase Orders, Commissioning Reports, Performance Certificate of successful operation from the procurer. | 1. As per the location of the site a lot of dew will be accumulated on the PV modules which on cleaning will create muck and will not be properly cleaned from dry type microfiber based brushes. 2. Also as per the supplier qualification any model of the robotic type cleaning can be used. Kindly clarify. | Technical | 1. Please refer Amendment - 1. 2. The terms and conditions of the tender document shall prevail.

## Amendment - 1
Tender No : SECI/C&P/PMC/11/0002/2021-22
Tender for Design, Engineering, Supply, Construction, Erection, Testing, commissioning and O&M of 5 MW (AC) Grid connected Saffron based Agro-Solar PV Project at Pampore, Pulwama, JK, India
S. No. | Section | Page No. | Clause | Original Version | Amendment
1 | Section -I IFB | 9 of 10 | (O)
2 | Section -I IFB | 10 of 10 | 6 (iii) | (iii) Third Contract (O&M Part): For providing Comprehensive operation & maintenance of the Solar PV plant for 15 (Fifteen) years from the date of Operational Acceptance, as detailed in technical specification including supply and storage of all spare parts, consumables, repairs/ replacement of any defective equipment etc. | (iii) Third Contract (O&M Part): For providing Comprehensive operation & maintenance of the Solar PV plant for 10 (Ten) years from the date of Operational Acceptance, as detailed in technical specification including supply and storage of all spare parts, consumables, repairs/ replacement of any defective equipment etc.
3 | Section -III BDS | 2 of 5 | 1
4 | Section -III BDS | 3 of 5 | 9
5 | Section-VIII Format for SOR | - | Schedule-1/SOR-1 | - | Please find attached the updated SOR Sheet.Bidders are required to quote their respective prices in the revised SOR sheet only & the earlier SOR will not be valid.
6 | Section-V Special Conditions of | 4 of 9 | 10 | Replace the existing clause by following: Against EPC/ LSTK & O&M Contract of the project, within 30 (Thirty) days from the issuance of the Notification of Award/ Letter of Intent/Letter of Award, the successful bidder shall furnish unconditional and irrevocable individual Bank Guarantees issued by any Nationalized Banks in the manner as mentioned below. The Contract Performance Security shall be in the form of Bank Guarantee only and shall be in the currency of the Contract and will be issued in the name of the Owner as “Jammu & Kashmir State Power Development Corporation Limited, Srinagar, Jammu & Kashmir, India” The Contract Performance Security against this Contract need to be furnished as mentioned below: 1. The value of the Contract Performance Security shall be 4% (Four percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 135 Months (12 Months Project commissioning period + 120 Months O & M Period + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of one year and the same may be extended every year till completion of the total 135 months period. | Replace the existing clause by following: Against EPC/ LSTK & O&M Contract of the project, within 30 (Thirty) days from the issuance of the Notification of Award/ Letter of Intent/Letter of Award, the successful bidder shall furnish unconditional and irrevocable individual Bank Guarantees issued by any Nationalized Banks in the manner as mentioned below. The Contract Performance Security shall be in the form of Bank Guarantee only and shall be in the currency of the Contract and will be issued in the name of the Owner as “Jammu & Kashmir State Power Development Corporation Limited, Srinagar, Jammu & Kashmir, India” The Contract Performance Security against this Contract need to be furnished as mentioned below: 1. The value of the Contract Performance Security shall be 3% (Three percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 135 Months (12 Months Project commissioning period + 120 Months O & M Period + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of one year and the same may be extended every year till completion of the total 135 months period.
7 | Section VII | Add Annexure - I Height of Structures present within proposed boundary | - | - | Annexure - I 'GT_Pampore_Structures_height' is added in Section VII
8 | General | Wherever Applicable | Wherever Applicable | - | Jammu & Kashmir Power Development Corporation Limited should be read as Jammu & Kashmir State Power Development Corporation Limited wherever mentioned in the entire tender document.
9 | Section-VII | 2 of 2 | - | Annexure - F: Tender Drawings – Existing Main Control Room | Annexure - F: Tender Drawings
10 | Section-VII(A) Scope of Works | 3 of 16 | 1 | … Ownership - Jammu and Kashmir Power Development Corporation Limited ... | … Ownership - Jammu and Kashmir State Power Development Corporation Limited ...
11 | Section-VII(A) Scope of Works | 4 of 16 | 1
12 | Section-VII(A) Scope of Works | 4 of 16 | 1 | … Capacity Utilization Factor at Substation End - 23% … | … Capacity Utilization Factor at Plant End - 23% …
13 | Section-VII(A) Scope of Works | 5 of 16 | 3.3 | All documents and drawings shall be submitted to the Employer both in soft as well as hard copies (5 nos.) for review and approval. Every drawing shall also be submitted in ‘*.dwg’ format. In case of design calculations done in spread sheet, editable (working) soft copy of the spread sheet shall also be submitted along with ‘pdf’ copies during every submission. The Employer shall return, as suitable, either soft or hard copies to the Contractor with category of approval marked thereon. ... | All documents and drawings (soft copy) shall be submitted to the Employer for review and approval. Every drawing shall also be submitted in ‘*.dwg’ format. In case of design calculations done in spread sheet, editable (working) soft copy of the spread sheet shall also be submitted along with ‘pdf’ copies during every submission. The Employer shall return to the Contractor with category of approval marked thereon. Five nos. of hard copies of approved documents and drawings shall be submitted to the Employer. ...
14 | Section-VII(A) Scope of Works | 7 of 16 | 4.9 | Inverter transformers of appropriate rating (2 × 2.5 MVA). | Inverter transformer of appropriate rating (5 MVA).
15 | Section-VII(A) Scope of Works | 8 of 16 | 4.1 | 33 kV Indoor Gas Insulated Switchgear (GIS) Panels including Vacuum Circuit Breakers, Current Transformers, Voltage Transformers, Relays and other accessories for complete protection. Outgoing feeder of GIS panel shall be rated for 10 MW. | 33 kV Indoor Gas Insulated Switchgear (GIS) Panels including Vacuum Circuit Breakers, Current Transformers, Voltage Transformers, Relays and other accessories for complete protection. Rating of outgoing feeders of GIS panel shall match with the rating of existing 33 kV line that runs from 200 MVA, 132/33 kV Grid Station to 10 MVA, 33/11 kV Substation.
16 | Section-VII(A) Scope of Works | 8 of 16 | 4.11 | ABT meters with all necessary metering rated CTs and PTs at the plant take-off point as well as at the interconnecting substation as per CEA Metering Regulations 2006 as amended time to time and state metering code. | ABT meters with all necessary metering rated CTs and PTs as per CEA Metering Regulations 2006 as amended time to time and state metering code.
17 | Section-VII(A) Scope of Works | 8 of 16 | 4.12 | 33 kV Over Head Transmission Line / Under Ground Cable (rated for 10 MW) including Poles / Towers, Conductors, Insulators, Cable Termination Kits and associated accessories from Plant take-off point to Interconnecting Substation as per DISCOM / STU specifications / requirements including Right of Way, permits and approvals, DISCOM supervision and maintenance charges. | 33 kV Over Head Transmission Line / Under Ground Cable (rating shall match the existing 33 kV line that runs from 200 MVA, 132/33 kV Grid Station to 10 MVA, 33/11 kV Substation) including Poles / Towers, Conductors, Insulators, Cable Termination Kits and associated accessories from GIS panel (Existing Main Control Room) to Interconnection Point as per DISCOM / STU specifications / requirements including Right of Way, permits and approvals, DISCOM supervision and maintenance charges.
18 | Section-VII(A) Scope of Works | 8 of 16 | 4.13 | 33 kV Indoor / Outdoor Switchgear panel / bay and other associated accessories (rated for 10 MW) for integration of Solar PV Power Plant at the interconnecting substation as per DISCOM / STU specifications / requirements including replacement of substation equipment / materials, permits and approvals, DISCOM supervision and maintenance charges. | VOID
19 | Section-VII(A) Scope of Works | 10 of 16 | 5.11 | Installation, Testing and Commissioning of ABT meters with all necessary metering rated CTs and PTs at Plant take-off point as well as at Interconnecting Substation as per CEA Metering Regulations 2006 as amended time to time and state metering code. ABT Meters at plant take-off point shall be installed inside existing Main Control Room. | Installation, Testing and Commissioning of ABT meters with all necessary metering rated CTs and PTs as per CEA Metering Regulations 2006 as amended time to time and state metering code.
20 | Section-VII(A) Scope of Works | 10 of 16 | 5.12 | Laying of AC cables from Inverter transformer to Plant take-off point along with termination at both the ends. | Laying of AC cables from Inverter transformer to GIS panel (Existing Main Control Room) along with termination at both the ends.
21 | Section-VII(A) Scope of Works | 10 of 16 | 5.13 | Installation, Testing and Commissioning of 33 kV Over Head Transmission Line / Underground Cable from Plant take-off point to Interconnecting Substation. | Installation, Testing and Commissioning of 33 kV Over Head Transmission Line / Underground Cable from GIS panel (Existing Main Control Room) to Interconnection Point.
22 | Section-VII(A) Scope of Works | 10 of 16 | 5.14 | Installation, Testing and Commissioning of 33 kV Switchgear panels / bay and associated accessories for integration of Solar PV Power Plant at the interconnecting substation including rearrangement of substation equipment / materials. | VOID
23 | Section-VII(A) Scope of Works | 11 of 16 | 6.4 | Construction of boundary wall around the entire plant area (wherever not available already). | VOID
24 | Section-VII(A) Scope of Works | 12 of 16 | 6.11 | Construction of foundation for 33 kV Overhead Transmission Line from Plant take-off point to Interconnecting Substation and associated civil works. | Construction of foundation for 33 kV Overhead Transmission Line from GIS panel (Existing Main Control Room) to Interconnecting Point and associated civil works, wherever applicable.
25 | Section-VII(A) Scope of Works | 12 of 16 | 6.12 | Construction of foundation and / or mounting structure for 33 kV Switchgear panels / bay and associated accessories for integration of Solar PV Power Plant at the Interconnecting Substation. | VOID
26 | Section-VII(A) Scope of Works | 12 of 16 | 7.1.1 | All statutory approvals/permissions and/or No Objection Certificates (NoC) etc. from DISCOM / STU for obtaining connectivity at the substation as per Project Particulars provided above. | All statutory approvals/permissions and/or No Objection Certificates (NoC) etc. from DISCOM / STU for obtaining connectivity at the Interconnection Point as per Project Particulars provided above.
27 | Section-VII(B) Technical Specifications | 9 of 101 | 1.4.3
28 | Section-VII(B) Technical Specifications | 27 of 101 | 6.3.1 | The switchgear panel shall be free standing, floor mounted, fully compartmentalized, metal enclosed construction. Each circuit shall have a separate vertical panel with required compartments for circuit breaker, cable termination, busbar and auxiliary control devices. Outgoing feeder of the GIS panel shall be rated for 10 MW. | The switchgear panel shall be free standing, floor mounted, fully compartmentalized, metal enclosed construction. Each circuit shall have a separate vertical panel with required compartments for circuit breaker, cable termination, busbar and auxiliary control devices.
29 | Section-VII(B) Technical Specifications | 32 of 101 | 6.10.2 | All feeders except main outgoing feeder shall be provided with digital Multi-Function Meter (MFM). Tri Vector Meter (TVM) shall be provided for the main outgoing feeder (in the HT Panel). Accuracy class of MFM shall be 0.2 and that of TVM shall be 0.2S. | All feeders shall be provided with digital Multi-Function Meter (MFM) with accuracy class of 0.2.
30 | Section-VII(B) Technical Specifications | 33 of 101 | 6.14.1 | Type Tests The switchgear panel shall be of type tested design. Type test reports of switchgear panel as per IS/IEC 62271-200 shall be submitted during detailed engineering. The tests should have been conducted on the similar equipment by NABL accredited laboratory. … | Type Tests The switchgear panel shall be of type tested design. Type test reports of switchgear panel as per IS/IEC 62271-200 shall be submitted during detailed engineering. The tests should have been conducted on the similar equipment by NABL accredited laboratory. Validity period of type tests conducted on the equipment shall be as per 'CEA Guidelines for the Validity Period of Type Test(s) conducted on Major Electrical Equipment in Power Transmission'. …
31 | Section-VII(B) Technical Specifications | 34 of 101 | 7.5 (ii) | … For HT cables (from inverter transformer to plant take off point), maximum voltage drop shall be limited to 0.5 % of the rated voltage. … | … For HT cables (from inverter transformer to 33 kV GIS panel), maximum voltage drop shall be limited to 0.5 % of the rated voltage. …
32 | Section-VII(B) Technical Specifications | 63 of 101 | 21.4 | The power evacuation system shall be rated for 10 MW. | The rating of power evacuation system shall match with the rating of existing 33 kV line that runs from 200 MVA, 132/33 kV Grid Station to 10 MVA, 33/11 kV Substation.
33 | Section-VII(B) Technical Specifications | 76 of 101 | 8 | Peripheral boundary Wall | VOID
34 | Section-VII Annexure-F (Tender Drawings) | 2 of 3 | - | New Page | Kindly refer the attachment - Area Utilization.
35 | Section-VII Annexure-F (Tender Drawings) | 3 of 3 | - | New Page | Kindly refer the attachment - Power Evacuation Scheme.
36 | Section-VII Annexure-G (Operation & Maintenance Agreement) | 38 of 45 | Annexure 2 Clause 1 (C) | Capacity Utilization Factor (CUF) for Solar Plant shall be calculated as per the following formula. …. | Kindly refer Annexure to Amendment-1.
37 | Section-VII(B) Technical Specifications | 94 | 23.1 | The PV Module Cleaning system shall be dry, Robotic type with microfibre-based brushes. | The PV Module Cleaning system shall be dry, Robotic type with microfibre or polymer-based brushes. The Contractor may optimise the no. of robot modules in the Robotic Cleaning System (including inter-row shifting of units) based on the battery capacity of individual units.
38 | Section-VII(B) Technical Specifications | 35 of 101 | 7.8.2 | Cables within transformer yard and switchyard shall be laid through RCC cable trench with supports. | Cables within the main (plant end) switchyard shall be laid through RCC cable trench with supports.
39 | Section-VII(B) Technical Specifications | 36 of 101 | 9.2 | New Addition | Air Circuit Breaker (ACB) Type Air-break Rated Current As per system requirement
40 | Section-VII(B) Technical Specifications | 53 of 101 | 15.9.2 | Operating System - Operating System and Database shall be of enterprise scale (RedHat Linux or equivalent Linux OS, Oracle/MySQL or equivalent DB), with required AMC for 5 years. | Operating System - Operating System and Database shall be of enterprise scale (RedHat Linux or equivalent Linux OS, Oracle/MySQL or Windows or equivalent DB), with required AMC for 5 years.
41 | Section-VII(B) Technical Specifications | 43 of 101 | 11.6 | Batteries and battery charger shall be warranted for minimum of 2 (two) years against all material/ manufacturing defects and workmanship. | Batteries and battery charger shall be warranted for minimum of 2 (two) years against all material/ manufacturing defects and workmanship from the date of supply.
42 | Section-VII(B) Technical Specifications | 82 of 101 | 12.4 | As specified above, the MMS support shall project minimum 200mm above FGL (Finished grade level) to avoid any damage to the MMS column/sub support due to direct contact of rain water/ surface run-off. This shall be ensured through either single stage construction of entire pile length including portion above FGL or by providing a collar (to be cast in second stage) which shall project min. 75mm in plan beyond the pile face and shall extend min. 250mm below GL. | As specified above, the MMS support shall project minimum 200mm above FGL (Finished grade level) to avoid any damage to the MMS column/sub support due to direct contact of rain water/ surface run-off. This shall be ensured through either single stage construction of entire pile length including portion above FGL or by two stage construction.
43 | Section-VII(B) Technical Specifications | 92 of 101 | 22.3 | In case of transformer oil tank capacity more ≥ 20000 litres, the soak pit shall be connected to a separate burnt oil pit through discharge pipe (300 mm dia) and shall be suitably sized to accommodate full oil volume (excluding free board above inlet pipe) of the transformer connected to it, without backflow. In this case the capacity of the soak pit may be reduced to min. 1/3rd of the total transformer oil volume. The burnt oil pit shall be further connected to oily water drainage system. The water shall be discharged into the nearest drain by gravity flow or pumping after suitable treatment as per statutory and code provisions. | In case of transformer oil tank capacity more ≥ 5000 litres, the soak pit shall be connected to a separate burnt oil pit through discharge pipe (300 mm dia) and shall be suitably sized to accommodate full oil volume (excluding free board above inlet pipe) of the transformer connected to it, without backflow. In this case the capacity of the soak pit may be reduced to min. 1/3rd of the total transformer oil volume. The burnt oil pit shall be further connected to oily water drainage system. The water shall be discharged into the nearest drain by gravity flow or pumping after suitable treatment as per statutory and code provisions.
44 | Annexure C - PG Test Procedure | 10 of 10 | A | Liquidated Damages for Shortfall in PR For every 0.01 shortfall in PR below the committed PR value, a penalty of 1% of the total Contract Value (i.e., total sum of all the Supply, Service and absolute value of O & M Contract) shall be levied. In case the Contract Performance Security has already been encashed on account of any default/delays, the penalty amount will be recovered from any due payments to the contractor. In case the Plant PR Shortfall is more than 0.05 than the specified PR value, then the total plant will be accepted on as-is basis & the total Contract Performance. Security submitted by the contractor will be forfeited & payments linked to operational acceptance will not be made. | Liquidated Damages for Shortfall in PR For every 0.01 shortfall in PR below the committed PR value, liquidated damages of 1% of the Contract Value shall be levied. However, if such Plant PR Shortfall is more than 0.05 than the specified PR value & if it breaches such specified PR value, then the total plant will be accepted on "as-is basis" & no payments will be made to the contractor perataining to the "Operation Accpetance" milestone in line with the defined payment terms. However, any other earlier pending/running payments as may be applicable, will be paid to the contractor as usual.
45 | Section-VII(B) Technical Specifications | 8 of 101 | 1.4.2
46 | Section-V Special Conditions of | 4 of 9 | 9 | Add following to the existing clause: 20.4 The Time for Completion for whole of the facilities means the timelines provided for commissioning in line with the SCC clause No 3 above. 20.5 No bonus will be given for earlier Commissioning of the Facilities or part thereof. | Add following to the existing clause: 20.4 The Time for Completion for whole of the facilities means the timelines provided for commissioning in line with the SCC clause No 3 above. 20.5 No bonus will be given for earlier Commissioning of the Facilities or part thereof. 20.6 The overall ceiling related to any kind of Liquidated Damages pertaining to this tender including LDs related to completion period, PR/CUF or any other LD as defined in the tender document is restricted to maximum 10% of the total contract value, excluding the case as mentioned under Sr No 44 Amendment 1 wherein the Plant PR Shortfall is more than 0.05 than the specified PR value.