Electronics City Industrial Township Authority

No. 7 (P), West Phase, Electronics City, Bangalore: 560 100

Phone: 080-4660 2222

Website: www.elcita.in

*****

DESIGN, SUPPLY, INSTALLATION, TESTING, AND COMMISSIONING INCLUDING WARRANTY OF GRID CONNECTED 100KWp SOLAR ROOFTOP PLANT AT 16 TPD SWM FACILITY,EAST PHASE, ELECTRONICS CITY, BENGALURU-560100.

TABLE OF CONTENTS

- Introduction…………………………………………………………………………………...3

  - Executive Summary

  - Introduction

- Evaluation Process………………………………………………………………………...… 3

2.1   Pre-Qualification Criteria

2.2 Work requirement Criteria

- General instruction to bidder………….………………………  ………………….......... .. .4

3.1 General instruction

3.2 Bidders scope

3.3 Security deposit

3.4 Earnest Money Deposit

- Terms and conditions…………………………………………………………. …................5

- Annexure I………………… ………………………………………………………………... 9

5.1 Self Declaration Certificate

# Introduction

## Executive Summary

ELCITA (Electronics City Industrial Township Authority) was formed to administer Electronics City Industrial Township Area with the powers of a municipality. Its core functionality is to collect taxes and statutory payments to meet its objectives in its area of operation of estate management. Its mandates include maintenance of municipal services of estate including civic amenities, sustainability, safety, traffic management, and regulation, granting approvals relating to building, Khata, trade licenses, town planning & ensuring a ‘future safe’ estate.

## Introduction

ELCITA invites a tender for design, supply, installation, testing, and commissioning of a 100 KWp solar roof top plant at Sustainability Park located at East Phase of Electronics City .  It should be a grid-connected solar plant.

ELCITA, through this tender targets installation of Grid-Connected Roof Top Solar Pv plants On The Rooftops of 16 TPD SWM Building.    The generated solar power may be utilized for captive application and the surplus power will be fed to the grid. The aim is to reduce the fossil fuel-based electricity load on main grid and make building self-sustainable from the point of electricity, to the extent possible.

# Evaluation Process

### 2.1.   Pre-Qualification Criteria

The Proposal failing to meet the pre-qualification eligibility criteria mention below shall be rejected and shall not be considered for technical evaluation.

| Sr. No. | Basic Requirement | Specific Requirement | Document Required |
| --- | --- | --- | --- |
| PQ 1 | Legal Entity | Bidder should be registered in India and should have been in operation for at least 5 years as on date of submission of the bid. | Copy of Certificate of Incorporation/ Registration. |
| PQ 2 | Similar Experience | The bidder should have successfully executed/completed in last 3 years to be reckoned from bid due date, at least one single contract as design, supply, installation, testing, and commissioning of a solar rooftop plant | Submit Copies of Work done/Work Order/Agreement |
| PQ 3 | Company’s Financial Profile | Bidder should have an annual turnover of minimum Rs. 5 Crore for the last 3 financial years (2019-20 2020-21,& 2021-22). | Attach the annual turnover Certified By CA |
| PQ 4 | Self-Declaration Certificate | Bidder shall not be under a declaration of ineligibility for corrupt or fraudulent practices with any of the State government/ Central Government / semi government / PSU / Municipal agencies in India at the time of submission. | Annexure –1 (Letter Head) |
| PQ 5 | Local Presence and other documents to be submitted | Bidder should have office in Bangalore from last 3 years | List and address of offices in Bangalore with GST Registration. |
| PQ 6 | Test Reports | The PV modules used must qualify to the latest edition of IEC PV module qualification test or equivalent BIS standards Crystalline Silicon Solar Cell Modules IEC 61215/IS14286. | Copy of the reports has to attached. |

## Work requirements criteria

| Sr. No | Criterion | Criterion Type | Mandatory |
| --- | --- | --- | --- |
| TQ.1 | Company Registration Certificate/ ELCITA Registration | Capabilities of Vendor | Within Expiry Date |
| TQ.2 | GST Registration Certificate | Others | GST Registration Certificate should be in the Present Company address |
| TQ.3 | Last Three Year Audited Annual Turnover Certificate | Financial Status | Certified By CA |
| TQ 4 | Work Done Certificate of manufacturer/supplier. | Experience | Work Order/Work done Certificate |
| TQ 5 | Self-Declaration Certificate (Annexure 1) | Others | Should be in Letter Head |
| TQ 6 | Detailed Delivery Schedule with Time of Completion | Others | Detailed Schedule |

## Technical Evaluation Criteria

| Sr. No | Technical Evaluation Criteria | Points |
| --- | --- | --- |
| TQ.1 | Company’s Financial Profile | 20 |
|  | Bidder should have average annual turnover of Rs. 5 crore for the last 3 financial years (2019-20, 2020-2021 and 2021-22) |  |
|  | >= Rs.5 Crore | 20 |
|  | < Rs. 5 Crore | 10 |
| TQ.2 | Relevant Experience | 30 |
|  | The Bidder should have installed & commissioned at least one Grid connected Solar PV Power Project having a capacity of not less than 100 KW which should have been commissioned at least six months prior to Techno-Commercial Bid Opening date & should be in successful operation for last 2 year prior to Techno-Commercial bid opening date. >=100 KWp—30 Marks <100 KWp to equal 50 KWp – 20 Marks <50KWp—10 Marks Need to submit Completion certificate /Work order/Agreement. |  |
| TQ3 | The list of the project commissioned last 5 years prior to Techno-Commercial Bid Opening date, indicating whether the project is grid connected, along with a copy of the Commissioning certificate and Work order / Contract / Agreement/ from the Client/Owner shall be submitted. More than 10 projects- 10 Marks Less than 5 projects- 5 Marks | 10 |
| TQ 4 | Technical Requirements | 40 |
|  | Certification from the customers Certification from 10 satisfied customers– ----------------10 Marks 10 certificates and above = 10 marks Below 10 certificates, each certificate will carry 2 marks . IOT dashboard (Integration IOT solar panel to dashboard) ---------10 Marks More than or equal to 1 integration----- 10 Marks Less than 1 integration —5 Marks The rated output power of any supplied module shall have tolerance of +4%.The bidder should submit the test reports.—10 Marks Equal or less than + 4% --- 10 Marks Greater than +/- 4% --- 5 Marks Bidder has to show Planned plant capacity v/s actually achieved capacity of previous installed plants (Test report from NABL Authorized lab) - 5 Marks Less Than 1 project--- 1 Marks If it is more than 1 projects each project will carry 1 marks. Additional features in terms of smart and hardware extra marks.---5 Marks Each features will carry 1 marks. |  |

## Technical Scoring and Evaluation

- This is a Quality & Cost Based Selection (QCBS).

- Technical Score (Ts) carries 70% of the weightage, while Relative Financial Score (RFs), to be calculated as per Section – 2.2, is given 30% weightage.

- The Total Technical Score (Ts) will be calculated out of 100 Marks and shall be evaluated as below.

- The Bidder has to score Minimum Qualifying Marks as below: - Overall Technical Evaluation: minimum 70 Points, The Bidders scoring marks less than the minimum qualifying marks as mentioned above shall be disqualified for Commercial Bid Opening.

## Commercial Scoring and Evaluation

  - This is a Quality & Cost Based Selection (QCBS)

  - The Relative Financial Score (RFs) carries 30% of the weight age, while the Technical Score (Ts), calculated as per Section – 2.1, is given 70% weight age.

  - The Commercial Bids of Technically Qualified bidders will be opened on the prescribed date in the portal.

  - The Relative Financial Score (RFs) of the bidder for the Commercial Bid Component as calculated below

    - The bidder with Lowest Qualifying Commercial Bid (CL) will be awarded 100 marks

    - The Relative Financial Score of another qualifying bidder shall be computed as below

  - Relative Financial Score of the Bidder (RFs) = (CL/ Commercial Bid of the respective Bidder) X 100   (Adjusted to two decimal places)

  - The bid price will include all taxes and levies and shall be in Indian Rupees and mentioned separately.

## Final Composite Bid Score and Evaluation

  - Technical Score (Ts), as per Section – 2.2, and Relative Financial Score (RFs), as per Section – 2.4., secured by each bidder will be considered for computing the Final Composite Bid Score.

  - The bidder securing the highest Composite Bid Score will be adjudicated as the most responsive Bidder for award of the Project.

  - The overall score will be calculated as follows: -

  - CBs= 0.70 * Ts + 0.30* RFs

Where, CBS = Final Composite Bid Score.

  - Ts = Total Technical score of the qualifying bidder

  - RFS = Total Relative Financial Score of the qualifying bidder.

- The preferred bidder shall be the agency securing the highest Final Composite Score.

- In the event of two or more Bidders securing the same composite score, then ELCITA reserves the right to Declare the bidder whose technical score is highest, among the bidders who have secured exactly the same composite score as preferred bidder Or adopt any other method as decided by ELCITA.

- ELCITA reserves the right to confirm the preferred bidder as successful bidder subject to negotiations and approval of competent authority.

# General Instructions to Bidder:

## General Instructions

These are the Following criteria’s that the Bidder has to comply with, failing which the BID will be rejected:

- All figures of costs, project values and others shall be mentioned in Indian Rupees only.

- No Tax exemptions are applicable.

- All queries shall be sent to ELCITA within a week of bid announcement, and there will be pre-bid meeting if required after the first week.

- Bidders need to attach all the requested documents in PDF format.

- The entire attached document should be well within expiry date.

- Bidders need to show all the Original Documents before evaluation.

- Bidder should submit detailed Bill of Quantities ( BOQ) after awarding the work.

# Terms and Conditions

A. General Conditions:

- Commercial to be uploaded through e-tendering portal of Government of Karnataka. (Date & time as mentioned in the e-portal)

- Submit a self- declaration that they have not been blacklisted by any Government agency or any Company / Government department or agency at any point of time. Certificate format attached (Ref: Annexure 1). Such self-declaration shall be given by the Successful Bidder on an annual basis to ELCITA

- Payment will be made after the certification issued by ELCITA Project Engineer & Operations manager ELCITA.

- BIDDER shall make their own arrangements for vehicle transportation, required equipment’s for erection and unskilled labor support. The welfare and all other statutory measures shall be implemented at their own cost by BIDDER.

- BIDDER quote is less than ELCITA the difference of amount should be paid through DD to ELCITA, and the same will be retuned back after completion of work.

- Bidder should visit the site before bidding.

B. Variations & Additions:

This is a fixed rate contract & rates will remain constant for the entire Agreement period and till the completion of the construction the date of Agreement.

C. Taxes:

- All rates quoted by and accepted by ELCITA are exclusive of taxes (GST).

- GST @ weighted average of 13.8% will be paid for the Bid Amount accepted by ELCITA.

- Any Taxes & cess with respect to the works contract subsequent to the tender submission date will be to Vendor’s account.

D. Payment of Bills:

- Payment against running bills will be made within fifteen working days from the date of certification by ELCITA Project Monitoring Team.

- Final bill payment to be made within Twenty-five working days from the date of certification by ELCITA Project Monitoring Team.

E. Payment Terms

- Payment against running bills will be made within fifteen working days from the date of certification by ELCITA Project Monitoring Team.

- No advance will be paid for the work.

F. Others

- Delivery Schedule:

BIDDER shall complete the work as detailed in scope of work within a period of Sixty (60) days from the award of tender.

- Retention:

A total 5% of the contract value shall be deducted as Retention Amount from each running bill and the same will be released after a defect liability period of 12 months. The defect liability period shall start from the date of deployment after testing and acceptance. The Retention amount can be paid against submission of Performance Bank Guarantee of equal value, valid for the duration of the Defect Liability Period.

4) Liquidated Damages:

In case the supply is not completed on or before the dates specified in the contract, a penalty shall be levied at the rate of 0.5% of the contract value for each week of delay. However, the total penalty levied shall not exceed 5% of the total contract value.

5) Payment Schedule:

Bills will be submitted, and payment shall be made as per Para C & D.

6) Termination of Contract:

If at any stage after the signing of the agreement, it is noticed that there is a substantial delay of more than fifteen (15) days from the schedule as mentioned in Scope of work, ELCITA will have the option to terminate the contract without assigning any reasons; under such situation BIDDER is required to pay back all amounts paid with 18 % (eighteen percent) interest p.a. without any delay, dispute, demur, etc.

7) Insurance:

BIDDER shall not have any claim regarding the safety of their tools, plant, workmen and they shall keep ELCITA free from all such liabilities. BIDDER shall take care of all such claims and not raise the same to ELCITA. BIDDER shall take workmen compensation policy for its workers and a copy of the same shall be provided to ELCITA.

8) Safety:

BIDDER shall be entirely responsible for the safety of the workers during supply. BIDDER shall follow the various Indian Standard Safety Codes during execution of Luminaries installations.

9) JV/Subcontracting & Assignment:

Joint venture/ Consortiums are not allowed with consent from ELCITA after complete disclosure during tendering process. BIDDER shall not assign or subcontract the Services to any third party without the prior written consent of ELCITA.

10)  Other Terms and Conditions:

- All bills will be in the name of "Electronics City Industrial Township Authority"

- Income Tax shall be deducted from the running account bills at the prevailing rates.

- Payments made to BIDDER will be inclusive of all taxes etc.

11) Confidentiality:

- Both Parties hereby undertakes and assures that any data, information and documents, trade secret, Design, financial information relating to both parties shall always be kept confidential by both parties & shall not be divulged or cause or allow the same to be disclosed to any person/persons whatsoever Whether in the employment of the parties or otherwise (except the specified employees of the parties having need to know and who are aware that it is confidential and bound to treat it as such) without the Express, prior written permission and consent of the other party. However, either party may disclose the information, which is available either in the public domain or the other party, is required to disclose By law. In the event of disclosure by any party being not within the exceptions hereinabove mentioned, the Disclosing party shall be liable to pay direct, monetary, incidental, special and/or consequential

- Damages suffered by the other party, arising out of such disclosure.

12) Indemnity:

BIDDER shall indemnify, defend, hold and keep indemnified, ELCITA its employees, representatives, other consultants etc. from and against all actions, suits, claims, costs, fines, judgments, liabilities and demands brought or made against ELCITA in respect of any matter of things done or omitted to be done by BIDDER or BIDDER’s employees, representatives, agents, contractors, etc. in the execution of or in connection with this Agreement and/or the Services, or BIDDER and or BIDDER’s employees, representatives, agents etc. performance under this Agreement and against any loss or damage to ELCITA in consequence of any action or suit being brought against ELCITA or ELCITA’s employees, representatives, agents etc. for anything done or omitted to be done in the provision of the Services under this Agreement, including but not limited to non-compliance with provisions of the Agreement, violation of applicable laws and regulations of any and all government authorities, non-obtainment of relevant licenses and permits etc. The obligations of BIDDER under this clause shall survive till the expiry of the Agreement. BIDDER agrees and undertakes that ELCITA shall have no liability whatsoever for any loss or injury or damage caused to property/any third party/person/ELCITA’s employees, representatives, agents etc. by any act of commission or omission of the Bidder or by BIDDER’s personnel assigned to perform the Services under this Agreement or otherwise.

13) Security Deposit:

The Security deposit 5% of the contract value to be paid to M/s Electronics City Industrial Township Authority (ELCITA) through DD/PBG, before awarding the work. This will be refunded after successful completion of the project. No interest is paid on Security deposit.

Annexure 1

SELF DECLARATION CERTIFICATE

1. I, _________________________ Director/ authorized signatory of the company, mentioned above, is competent to sign this declaration and execute this tender document.

2. I have carefully read and understood all the terms and conditions of the tender and undertake to abide by them except the changes suggested by us in our proposal.

3. The information / documents furnished along with the above application are true and authentic to the best of my knowledge and belief. I/We am/ are aware of the fact that furnishing of any false information / fabricated document would lead to rejection of my tender at any stage besides liabilities towards prosecution under appropriate law.

4. I, do hereby certify that at the time of submission, our company has not been blacklisted by any of the Govt Departments/PSUs Banks with which the company had contracted for supply of similar equipment in India or abroad

Seal & Signature of authorized person

Technical Specifications:

The proposed projects shall be commissioned as per the technical specifications given below.

A Grid Tied Solar Rooftop Photo Voltaic (SPV) power plant consists of SPV array, Module Mounting Structure, Power Conditioning Unit (PCU) consisting of Maximum Power Point Tracker (MPPT), Inverter, Controls, Protections, interconnect cables and switches. PV Array is mounted on a suitable structure. Grid tied SPV system is without battery and should be designed with necessary features to supplement the grid power during day time. Components and parts used in the SPV power plants including the PV modules, metallic structures, cables, junction box, switches, PCUs etc., should conform to the BIS or IEC or international specifications, wherever such specifications are available and applicable.

Solar PV system shall consist of following equipment’s/components.

- Solar PV  modules consisting of  required  number of  Mono Crystalline  PV modules.

- Grid interactive Power Conditioning Unit with Remote Monitoring System

- Mounting structures

- Junction Boxes.

- Earthing and lightning protections.

- IR/UV protected PVC Cables, pipes and accessories

The G+1 Single building having two way pitched soft roof is oriented along east – West direction instead of the optimal North – South Direction. Design to be made such that the solar panel will be laid over the existing slope without raising the panel. Vendors to comprehend the existing design impediment and produce a design solution for generating 100KW DC sized system with optimal number of PV’s.

  - SOLAR PHOTOVOLTAIC MODULES:

    - The PV modules used should be made in India.

    - The PV modules used must qualify to the latest edition of IEC PV module qualification test or equivalent BIS standards Crystalline Silicon Solar Cell Modules IEC 61215/IS14286. In addition, the modules must conform to IEC 61730 Part-2- requirements for construction & Part 2 – requirements for testing, for safety qualification or equivalent IS.

- For the PV modules to be used in a highly corrosive atmosphere throughout their lifetime, they must qualify to IEC 61701/IS 61701

- The total solar PV array capacity should not be less than 100KWp and should comprise of solar crystalline modules of minimum 535 Wp and above wattage. Module capacity less than minimum 535 watts will not be accepted.

- Protective devices against surges at the PV module shall be provided. Low voltage drop bypass diodes shall be provided.

- PV modules must be tested and approved by one of the IEC authorized test centers.

- The module frame shall be made of corrosion resistant materials, preferably having anodized aluminum.

- The bidder shall carefully design & accommodate requisite numbers of the modules to achieve the rated power in his bid.

- Other general requirement for the PV modules and subsystems shall be the Following:

  - The rated output power of any supplied module shall have tolerance of     + 4%.

  - The peak-power point voltage and the peak-power point current of any supplied module and/or any module string (series connected  modules) shall not vary by more than 2 (two) per cent from the respective arithmetic means for all modules and/or for all module strings, as the case may be.

  - I-V Curves at STC should be provided by bidder.

    - Modules deployed must use a RF identification tag.  The following information must be mentioned in the RFID used on each modules (This can be inside or outside the laminate, but must be able to withstand harsh environmental conditions).

- Name of the manufacturer of the PV module

- Name of the manufacturer of Solar Cells.

- Month & year of the manufacture (separate for solar cells and modules)

- Country of origin (separately for solar cells and module)

- I-V curve for the module Wattage, Im, Vm and FF for the module

- Unique Serial No and Model No of the module

- Date and year of obtaining IEC PV module qualification certificate.

- Name of the test lab issuing IEC certificate.

- Other relevant information on traceability of solar cells and module as per ISO 9001 and ISO 14001

    - Warranties:

- Material Warranty:

  - Material Warranty is defined as: The manufacturer should warrant the Solar Module(s) to be free from the defects and/or failures specified below for a period not less than five (05) years from the date of sale to the original customer ("Customer").

  - Defects and/or failures due to manufacturing.

  - Defects and/or failures due to quality of materials.

  - Nonconformity to specifications due to faulty manufacturing and/or inspection processes. If the solar module(s) fails to conform to this warranty, the manufacturer will repair or replace the solar module(s), at the Owners sole option

- Performance Warranty:

  - The predicted electrical degradation of power generated shall be warranted for not more than 10% degradation in the first 10 years and not more than 20% degradation in 25 years.

  - Bidder shall have a EPR (Extended Producer Responsibility) for the solar panel.

- ARRAY STRUCTURE

- Hot dip galvanized MS mounting structures shall be used for mounting the modules/ panels/arrays. Fixing along the roof shall be done as stated in the technical specs.

- The Mounting structure shall be so designed to withstand the load  for the wind zone of the location where a PV system is proposed to be installed (Designed for 150+ kmph wind load).  It may be ensured that the design has been certified by a recognized Lab/ Institution in this regard and submit wind loading calculation sheet to [NAME OF THE ORGANISATION]. Suitable fastening arrangement such as grouting and calming should be provided to secure the installation against the specific wind speed.

- The mounting structure steel shall be as per latest IS 2062: 1992 and galvanization of the mounting structure shall be in compliance of latest IS 4759.

- Structural material shall be corrosion resistant and electrolytically compatible with the materials used in the module frame, its fasteners, nuts and bolts. Necessary protection towards rusting need to be provided either by coating or anodization.

- The fasteners used should be made up of stainless steel. The structures shall be designed to allow easy replacement of any module. The array structure shall be so designed that it will occupy minimum space without sacrificing the output from the SPV panels.

- Regarding civil structures the bidder need to take care of the load baring capacity of the roof and need arrange suitable structures based  on  the quality of roof.

- The total load of the structure (when installed with PV modules) on  the terrace should withstand the load.

- The minimum clearance of the structure from the roof level should be 100mm.

- JUNCTION BOXES (JBs):

- The junction boxes are to be provided in the PV array for termination of connecting cables. The J. Boxes (JBs) shall be made of GRP/FRP/Powder Coated Aluminum /cast aluminum alloy with full dust, water & vermin proof arrangement. All wires/cables must be terminated through cable lugs. The JBs shall be such that input & output termination can be made through suitable cable glands.

- Copper bus bars/terminal blocks housed in the junction box with suitable termination threads Conforming to IP65 standard and IEC  62208 Hinged door with EPDM rubber gasket to prevent water entry. Single / double compression cable glands. Provision of earthings. It should be placed at 5 feet height or above for ease of accessibility.

- Each Junction Box shall  have High quality Suitable capacity Metal Oxide Varistors (MOVs) / SPDs, suitable Reverse Blocking Diodes. The Junction Boxes shall have suitable arrangement monitoring and disconnection for each of the groups.

- Suitable markings shall be provided on the bus bar for easy identification and the cable ferrules must be fitted at the cable termination points for identification

- DC DISTRIBUTION BOARD:

- DC Distribution panel to receive the DC output from the array field.

- DC DPBs shall have sheet from enclosure of dust & vermin proof conform to IP 65 protection. The bus bars are made of copper of desired size. Suitable capacity MCBs/MCCB shall be provided for controlling the DC power output to the PCU along with necessary surge arrestors.

- AC DISTRIBUTION PANEL BOARD:

- AC Distribution Panel Board (DPB) shall control the AC power from PCU/ inverter, and should have necessary surge arrestors. Interconnection from ACDB to mains at LT Bus bar while in grid tied mode.

- All switches and the circuit breakers, connectors should conform to IEC 60947, part I, II and III/ IS60947 part I, II and III.

- The changeover switches, cabling work should be undertaken by the bidder as part of the project.

- All the Panel’s shall be metal clad, totally enclosed, rigid, floor mounted, air - insulated, cubical type suitable for operation on three phase / single phase, 415 or 230 volts, 50 Hz

- The panels shall be designed for minimum expected ambient temperature of 45 degree Celsius, 80 percent humidity and dusty weather.

- All indoor panels will have protection of IP54 or better. All outdoor panels will have protection of IP65 or better.

- Should conform to Indian Electricity Act and rules (till last amendment).

- All the 415 AC or 230 volts devices / equipment like bus support insulators, circuit breakers, SPDs, VTs etc., mounted inside the switchgear shall be suitable for continuous operation and satisfactory performance under the following supply conditions

| Variation in supply voltage | +/- 10 % |
| --- | --- |
| Variation in supply frequency | +/- 3 Hz |

- PCU/ARRAY SIZE RATIO:

- The combined  wattage  of  all  inverters  should  not  be  less  than  rated capacity of power plant under STC.

- Maximum power point tracker shall be integrated in the PCU/inverter to maximize energy drawn from the array.

- PCU/ Inverter:

As SPV array produce direct current electricity, it is necessary to convert this direct current into alternating current and adjust the voltage levels to match the grid voltage. Conversion shall be achieved using an electronic Inverter and the associated control and protection devices. All these components of the system are termed the “Power Conditioning Unit (PCU)”. In addition, the PCU shall also house MPPT (Maximum Power Point Tracker), an interface between Solar PV array & the Inverter, to the power conditioning unit/inverter should also be DG set interactive. If necessary. Inverter output should be compatible with the grid frequency. Typical technical features of the inverter shall be as follows:

- Switching devices	: IGBT/MOSFET

- Control	: Microprocessor /DSP

- Nominal AC output voltage and frequency  : 415V, 3 Phase, 50 Hz (In case single phase inverters are offered, suitable arrangement for balancing the phases must be made.)

- Output frequency	: 50 Hz

- Grid Frequency Synchronization range	: + 3 Hz or more

- Ambient temperature considered  : -20o C to 50o C

- Humidity        : 95 % Non-condensing

- Protection of Enclosure       : IP-20(Minimum) for indoor.

: IP-65(Minimum) for outdoor.\

- Grid Frequency Tolerance range  : + 3 or more

- Grid Voltage tolerance        : - 20% & + 15 %

- No-load losses         : Less than 1% of rated power

- Inverter efficiency(minimum)          : >93% ( In case of 10kW or above )

- Inverter efficiency (minimum )      : > 90% (In case of less than 10 kW)

- THD                                                   : < 3%

- PF                                                      : > 0.9

- Three phase PCU/ inverter shall be used with each power plant system (10kW and/or above) but In case of less than 10kW single phase inverter can be used.

- PCU/inverter shall be capable of complete automatic operation including wake-up, synchronization & shutdown.

- The output of power factor of PCU inverter is suitable for all voltage ranges or sink of reactive power, inverter should have internal protection arrangement against any sustainable fault in feeder line and against the lightning on feeder.

- Built-in meter and data logger to monitor plant performance through external computer shall be provided.

- The power conditioning units / inverters should comply with applicable IEC/ equivalent BIS standard for efficiency measurements and environmental tests as per standard codes IEC 61683/IS 61683 and  IEC  60068- 2(1,2,14,30) /Equivalent BIS Std.

- The charge controller (if any) / MPPT units environmental testing should qualify IEC 60068-2(1, 2, 14, 30)/Equivalent BIS std. The junction boxes/ enclosures should be IP 65(for outdoor)/ IP 54 (indoor) and as per IEC 529 specifications.

- The PCU/ inverters should be tested from the MNRE approved test centers / NABL /BIS /IEC accredited testing- calibration laboratories. In case of imported power conditioning units, these should be approved by international test houses.

- INTEGRATION OF PV POWER WITH GRID:

The output power from SPV would be fed to the inverters which converts DC produced by SPV array to AC and feeds it into the main electricity grid after synchronization.  In  case  of grid  failure,  or  low or  high voltage, solar  PV system shall be out of synchronization and shall be disconnected from the grid.

DATA ACQUISITION SYSTEM / PLANT MONITORING

- Data Acquisition System shall be provided for each of the solar PV plant.

- Data Logging Provision for plant control and monitoring, time and date stamped system data logs for analysis with the high quality, suitable PC. Metering and Instrumentation for display of systems parameters and status indication to be provided.

- Solar Irradiance: An integrating Pyranometer / Solar cell-based irradiation sensor (along with calibration certificate) provided, with the sensor mounted in the plane of the array. Readout integrated with data logging system.

- Temperature: Temperature probes for recording the Solar panel temperature and/or ambient temperature to be provided complete with readouts integrated with the data logging system

- The following parameters are accessible via the operating interface display in real time separately for solar power plant:

- AC Voltage.

- AC Output current.

- Output Power

- Power factor.

- DC Input Voltage.

- DC Input Current.

- Time Active.

- Time disabled.

- Time Idle.

- Power produced

- Protective function limits (Viz-AC Over voltage, AC Under voltage, Over frequency, Under frequency ground fault, PV starting voltage, PV stopping voltage.

- Efficiency of the generation of array .

- All major parameters available on the digital bus and logging facility for energy auditing through the internal microprocessor and read on the digital front panel at any time) and logging facility (the current values, previous values for up to a month and the average values) should be made available for energy auditing through the internal microprocessor and should be read on the digital front panel.

- PV array energy production: Digital Energy Meters to log the actual value of AC/ DC voltage, Current & Energy generated by the PV system provided. Energy meter along with CT/PT should be of 0.5 accuracy class.

- Computerized DC String/Array monitoring and AC output monitoring shall be provided as part of the inverter and/or string/array combiner box or separately.

- String and array DC Voltage, Current and Power, Inverter AC output voltage and current (All 3 phases and lines), AC power (Active, Reactive and Apparent), Power Factor and AC energy (All 3 phases and cumulative) and frequency shall be monitored.

- Computerized AC energy monitoring shall be in addition to the digital AC energy meter.

- The data shall be recorded in a common work sheet chronologically date wise. The data file shall be MS Excel compatible. The data shall be represented in both tabular and graphical form.

- All instantaneous data shall be shown on the computer screen.

- Software shall be provided for USB download and analysis of DC and AC parametric data for individual plant.

- Provision for Internet monitoring and download of data shall be also incorporated.

- Remote Server and Software for centralized Internet monitoring system shall be also provided for download and analysis of cumulative data of all the plants and the data of the solar radiation and temperature monitoring system.

- Ambient / Solar PV module back surface temperature shall be also monitored on continuous basis.

- Simultaneous monitoring of DC and AC electrical voltage, current, power, energy and other data of the plant for  correlation  with  solar  and environment data shall be provided.

- Remote Monitoring and data acquisition through Remote Monitoring System software at the project location with latest software/hardware configuration and service connectivity for  online  /  real time data monitoring/control complete to be supplied and operation and maintenance/control to be ensured by the supplier. Provision for interfacing these data on TSSPDCL server and portal in future shall be kept.

- METERING:

- The bidirectional electronic energy meter (0.5 S class) shall be installed for the measurement of import/Export of energy. The meters shall be provided by the BESCOM.

- POWER CONSUMPTION:

- Regarding the generated power consumption, priority need to give for internal consumption first and thereafter any excess power can be exported to grid.

- PROTECTIONS

The system should be provided with all necessary protections like earthing, Lightning, and grid islanding as follows:

  - LIGHTNING PROTECTION

The SPV power plants shall be provided with lightning &overvoltage protection. The main aim in this protection shall be to reduce the over voltage to a tolerable value before it reaches the PV or other sub system components. The source of over voltage can be lightning, atmosphere disturbances., etc. The entire space occupying the SPV array shall be suitably protected against Lightning by deploying required number of Lightning Arrestors. Lightning protection should be provided as per IEC 62305standard. The protection against induced high-voltages shall be provided by the use of metal oxide varistors (MOVs) and suitable earthing such that induced transients find an alternate route to earth.

  - SURGE PROTECTION

Internal surge protection shall consist of three MOV type surge-arrestors connected from +ve and –ve terminals to earth (via Y arrangement)

  - EARTHING PROTECTION

- Each array structure of the PV yard should be grounded/ earthed properly as per IS:3043-1987. In addition the lighting arrester/masts should also be earthed inside the array field. Earth Resistance shall be tested in presence of the representative of Elcita or Authorised representative as and when required after earthing by calibrated earth tester. PCU, ACDB  and DCDB should also be earthed properly.

- Earth resistance shall not be more than 5 ohms. It shall be ensured that all the earthing points are bonded together to make them at the same potential.

  - GRID ISLANDING:

- In the event of a power failure on the electric grid, it is required that any independent power-producing inverters attached to the grid turn off in a short period of time. This prevents the DC-to-AC inverters from continuing to feed power into small sections of the grid, known as “islands.” Powered islands present a risk to workers who may expect the area to be unpowered, and they may also damage grid-tied equipment. The Rooftop PV system shall be equipped with islanding protection. In addition to disconnection from the grid (due to islanding protection) disconnection due to under and over voltage conditions shall also be provided.

- A manual disconnect 4pole isolation switch beside automatic disconnection to grid would have to be provided at utility end to isolate the grid connection by the utility personnel to carry out any maintenance. This switch shall be locked by the utility personnel

- CABLES

Cables of appropriate size to be used in the system shall have the following characteristics:

- Shall meet IEC 60227/IS 694, IEC 60502/IS1554 standards

- Temp. Range:  –10oC to +80oC.

- Voltage rating 660/1000V

- Excellent resistance to heat, cold, water, oil, abrasion, UV radiation

- Flexible

- Sizes of cables between array interconnections, array to junction boxes, junction boxes to Inverter etc. shall be so selected to keep the voltage drop (power loss) of the entire solar system to the minimum. The cables (as per IS) should be insulated with a special grade PVC compound formulated for outdoor use.

- Cable Routing/ Marking: All cable/wires are to be routed in a GI cable tray and suitably tagged and marked with proper manner by good quality ferule or by other means so that the cable easily identified.

- The Cable should be so selected that it should be compatible up to the life of the solar PV panels i.e. 25years.

- The ratings given are approximate. Bidder to indicate size and length as per system design requirement. All the cables required for the plant provided by the bidder. Any change in cabling sizes if desired by the bidder/approved after citing appropriate reasons. All cable schedules/layout drawings approved prior to installation.

- Multi Strand, Annealed high conductivity copper conductor PVC type ‘A’ pressure extruded insulation or XLPE insulation. Overall PVC/XLPE insulation for UV protection Armoured cable for underground laying. All cable trays including covers to be provided. All cables conform to latest edition of IEC/ equivalent BIS Standards as specified below: BoS item / component Standard description Standard Number Cables	General Test and Measuring Methods, PVC/XLPE insulated cables for working   Voltage up to and including 1100 V, UV resistant for outdoor installation IS /IEC 69947.

- The size of each type of DC cable selected shall be based on minimum voltage drop however; the maximum drop shall be limited to 1%.

- The size of each type of AC cable selected shall be based on minimum voltage drop however; the maximum drop shall be limited to 2 %.

- CONNECTIVITY

The vendor will follow KPTCL/BESCOM Net metering guidelines for connecting to the Grid. KPTCL/BESCOM will provide the required meters to the vendor for installation.

The interconnection with the grid shall be as specified in the Distribution Code/Supply Code of the State, KPTCL/BESCOM Net metering guidelines and amended from time to time. The injection shall be compulsorily at the LT level of the distribution network

- TOOLS & TACKLES AND SPARES:

- After completion of installation & commissioning of the power plant, necessary tools & tackles are to be provided free of cost by the bidder for maintenance purpose. List of tools and tackles to be supplied by the bidder for approval of specifications and make from ELCITA .

- A list of requisite spares in case of PCU/inverter comprising of a set  of control logic cards, IGBT driver cards etc. Junction Boxes. Fuses, MOVs / arrestors, MCCBs etc along with spare set of PV modules be indicated, which shall be supplied along with the equipment. A minimum set of spares shall be maintained in the plant itself for the entire period of warranty and Operation & Maintenance which upon its use shall be replenished.

- DANGER BOARDS AND SIGNAGES:

Danger boards should be provided as and where necessary as per IE Act. /IE rules as amended up to date. Three signage shall be provided one each at battery –cum- control room, solar array area and main entry from administrative block. Text of the signage may be finalized in consultation with ELCITA.

- DRAWINGS & MANUALS:

- Two sets of Engineering, electrical drawings and Installation and O&M manuals are to be supplied. Bidders shall provide complete technical data sheets for each equipment giving details of the specifications along with make/makes in their bid along with basic design of the power  plant and power evacuation, synchronization along with protection equipment.

- Approved ISI and reputed makes for equipment be used.

- For complete electro-mechanical works, bidders shall supply complete design, details and drawings for approval  to ELCITA / KPTCL/BESCOM  before progressing with the installation work.

- PLANNING AND DESIGNING:

- The bidder should carry out Shadow Analysis at the site and accordingly design strings & arrays layout considering optimal usage of space, material and labor. The bidder should submit the array layout drawings along with Shadow Analysis  Report  to  ELCITA for approval.

- ELICTA reserves the right to modify the landscaping design, Layout and specification of sub-systems  and components at any stage as per local site conditions/requirements.

- The bidder shall submit preliminary drawing for approval & based on any modification or recommendation, if any. The bidder submit three sets and soft copy in CD of final drawing for formal approval to proceed with construction work.

- DRAWINGS   TO   BE   FURNISHED   BY   BIDDER   AFTER   AWARD   OF CONTRACT

- The Contractor shall furnish the following drawings Award/Intent and obtain approval

- General arrangement and dimensioned layout

- Schematic drawing showing the requirement of SV panel, Power conditioning Unit(s)/ inverter, Junction Boxes, AC and DC Distribution Boards, meters etc.

- Structural drawing along with foundation details for the structure.

- Itemized bill of material for complete SV plant covering all the components and associated accessories.

- Layout of solar Power Array

- Shadow analysis of the roof.

- SAFETY MEASURES:

The bidder shall take entire responsibility for electrical safety of the installation(s) including connectivity with the grid and follow all the safety rules & regulations applicable as per Electricity Act, 2003 and CEA guidelines etc.

- Integration with ELCITA CCC Dashboard.

- The vendor should share the real-time status of the Smart controller information to ELCITA - CCC / Centralized Management and Monitoring Software System through REST API (J SON Measuring and stored Electrical values – Voltage, Current, Frequency, Active power.

- The IoT controller/gateway system should be able to operate according to the present weather conditions such as sunlight or rainy day. Should be IP67/Adequate Protection should be catered for the gateway.

- The ELCITA administration should be able to see the real-time status of the Solar roof top System On ELCITA map view in the ELCITA-CCC System/ Centralized Management and Monitoring Software

- The IoT device should be able to communicate the system issue or failure to the ELCITA –CCC System / Centralized Management and Monitoring Software

- Vendor should specify the communication protocol between Solar roof top and gateway

- The vendor should specify for any subscription charges required.

- Fault Detection and Alerts:

- Alarm notification for solar roof top failures or fault.

- Auto failure detection.

- Should be capable of Over the Air (OTA) software update.

- Vendor application should have well-documented APIs for developing applications for Policy-based Management of Outdoor solar roof top pv plant.

- Vendor shall suggest future safe communication protocol and include any recurring costs

- Vendor shall include annual costs including license fee and communication charges if any.

- Reports & amp; MIS

- Power generation of Individual / Group / Zone for day/ week / month / year.

- Health status of Individual /Group / Zone for daily /week /month /years.

- MIS for energy efficiency will help management to take better decision for scheduling and policy making.