## Pre Bid Queries
“THE MANUFACTURING, TESTING, PACKING AND FORWARDING, SUPPLY AND TRANSPORTATION OF 1680 MWP DOMESTICALLY MANUFACTURED SOLAR PV MODULES WITH DOMESTICALLY MANUFACTURED SOLAR CELLS”
Tender No : SECI/C&P/OP/11/0001/2022-23
Sl. No. | Tender Section | Page No. | Clause No | Description as per Tender Document | Queries | Category (Finance/Technical/Contractual) | Clarifications
1 | I | 11 of 11 | 6.0 (i) | Purchase & Service Order: For providing the Ex Works-Supply, materials including mandatory spares and any other supplies specified in the Tender Documents under the scope of Supply. And for all services i.e., including Transportation and Insurance of all supplies till site, Unloading, and Handling at Site in respect of all the supplies and any other services specified in the Contract | Unloading should not be in the scope of supplier as per common industry practise as the same is borned by the purchaser as this is a material supply tender not an EPC supply tender. Request you to please consider the same. | Contractual | The terms and conditions of the tender document shall prevail.
2 | IV | 27 of 46 | 40.3 | Execution of Supply: The Supplier shall arrange for transportation, loading & unloading, local sifting, EAR insurance and safe storage of materials at project site at his own cost & risk. | Unloading, local shifting and EAR insurance and safe storage should be in the scope of Owner / EPC company. The tender is of module supply and as a supplier we don’t have any provision to cater the same at the site. Request you to please consider the same. | Contractual | The provision for local shifting after delivery and EAR Insurance is removed form Contractor scope. Please refer to Amendment-1 for the same. And unloading of materials at site will be in the scope of the Supplier.
3 | V | 4 of 8 | 6-25.3 | Defective Modules: Modules found defective/damaged during the random physical/visual inspection or not having all weather worthy packing or improper palletizing or defects arising due to improper unloading. | The scope is of module supply and as per general industry practice, the unloading is not carried by Module supplier. This is to tbe borne by EPC / Owner. | Contractual | The terms and conditions of the tender document shall prevail.
4 | VII | 3 of 17 | 1.1 | Scope of Supply: The scope of supply includes Manufacturing, Testing, Packing and Forwarding, Transportation to Site and Unloading of domestically manufactured Solar PV Modules with domestically manufactured solar cells. | The scope is of module supply and as per general industry practice, the unloading is not carried by Module supplier. This is to the borne by EPC / Owner. | Contractual | The terms and conditions of the tender document shall prevail.
5 | IV | 15 of 46 | 21.1 | Liquidated Damages (LD): Subject to Force Majeure Clause, if the Supplier fails to comply with the Time of Supply or any extension thereof in accordance with timelines as mentioned under the SPC, then the Supplier shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the Contract Price for the whole of the supplies as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the supplies. | As per standard industry practice, the LD clause should be levied on remaining supplies / unsupplied portion of the contract qty, not on the overall contract price. Request you to revise the same. | Contractual | Kindly refer Amendment-1.
6 | IV | 35 of 46 | 57 | Watch & Ward and Lighting: The Supplier shall provide and maintain at its own expense all lighting, fencing, watch and ward wherever necessary for the proper execution and the protection of the supply stockyard at site, or for the safety of the Owners and occupiers of adjacent property and for the safety of the public during the entire supply period. | As supplier is scope is limited to module supply only, the sole responsibility should be with the owner. Request you to please consider the same. | Contractual | Kindly refer Amendment-1.
7 | III | 3 of 7 | 1.2 | TECHNICAL ELIGIBILITY CONDITIONS Bidders can participate through any one of the below mentioned qualifying routes. The bidder shall be considered meeting Technical Eligibility criteria either from Route I or Route II. | Are we eligible to bid from two different subsidiary companies under the same group company OR One from Parent company and other from subsidiary company. One from Route I and another from Route II? | Contractual | NOT ALLOWED
8 | IV | 21 of 46 | 29 | The Supplier shall provide and maintain an office at the site for the accommodation of his agent and staff (With meeting room) and such office shall be open at all reasonable hours to receive instructions, notice or other communications. The Supplier shall make provisions and arrangements at site locations for temporary office (Porta cabin) including all basic amenities having electricity, furniture, Air Conditioning, Sanitation, toilet facilities, etc. at his own cost on behalf & purpose of the Owner and his staff and shall get the clearance of local authorities for setting up/supply of such facilities. Bidders are required to consider all such temporary office supply cost into his account, while bidding. These facilities shall be provided till the final handing over of the supply to the Owner. The Supplier shall ensure that the area is kept clean and sanitary conditions are maintained as laid down by the local authorities controlling the area. Further Supplier shall also provide & ensure availability of required Vehicle (Preferably SUV Segment Vehicles requiring Off Roading) with driver and fuel/Maintenance/Consumables etc. for the purpose of Mobility in and around the site for official purposes for the Owner & its staff. The vehicle as mentioned is to be provided during project supply and inspection by SECI as per requirement, failing which SECI shall have full right for alternate arrangement at the risk & cost of the Supplier | The suppliers should be limited to delivering material at the site store location. The setting up of office and its maintenance along with staff should not be a compulsion in the module supply contract. The vehicle supply / provision should not be in the scope of module supplier. | Contractual | Kindly refer Amendment-1.
9 | IV | 29 of 46 | 44.2 | The Supplier shall ensure that all the supplies are properly dispatched. The Supplier shall at its own risk and expense transport all the supplies and the Supplier’s Equipment to the Site by the mode of transport that the Supplier judges most suitable under all the circumstances. Supplier shall be responsible to assess in advance suitability of access roads, bridges, culverts, etc. for transportation of ODC shipments, if any and arrange to transport them accordingly. In case, the Supplier decides to transport the Goods by road within Owner’s country, then such Goods must necessarily be transported through a registered common carrier as per Carriage by Road Rules 2011 of Central Government of India. | The supplier can only plan in advance for the access of roads only if the locations informed prior. Approach road to the site from the national highway or state highway should be in the scope of owner. | Contractual | Site location will be informed to the successful suppliers well in advance before the actual supply date. The supplier needs to ensure smooth and damage free supplies till site considering road factors.
10 | IV | 35 of 46 | 56 | Disposal of Scrap The term ‘Scrap’ shall refer to scrap/ waste/ remnants arising out of the unpacking of equipment, supply debris, breakage of modules, fabrication of structural steel supply and piping supply at the project site in the course of execution of the contract and shall also include any wastage of cables during the termination process while installing the cables. | The Suppliers scope should be limited to transportation to site (Excluding Unloading). So disposal of any type of scrap after unloading should be in the scope of Owner only. Request you to consider the same. | Contractual | Kindly refer Amendment-1.
11 | V | 3 of 8 | 6 | Contract Performance Security: The value of the Contract Performance Security shall be 3% (Three) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 31 Months (16 Months Project completion period) + 12 months of Defect Liability Period + 03 Months additional) from the date of its issuance. | We request you to kindly keep the validity of CPS for the period of DLP i.e. 1 year from the date of its issuance | Contractual | The terms and conditions of the tender document shall prevail.
12 | Part B | 181 | 1.1 | IS 14286: Part 1: 2019 | Available IS 14286 : 2010/ IEC 61215 : 2005 for acceptance. IEC 61215 2021 available. Kindly accept the same | Technical | IEC 61215:2021 is acceptable.
13 | Part B | 181 | 1.1 | IS/IEC 61730-1: 2016 | Available IS/IEC 61730 (PART 1) : 2004 for acceptance IEC 61730 2016 available. Kindly accept the same | Technical | IEC 61730-1:2016 is acceptable.
14 | Part B | 181 | 1.1 | IS/IEC 61730-2: 2016 | Available IS/IEC 61730 (PART 2) : 2004 for acceptance. IEC 61730 2016 available. Kindly accept the same | Technical | IEC 61730-2:2016 is acceptable.
15 | Part B | 181 | 1.1 | IS/IEC 61701: 2011 | Available IEC 61701:2020 for acceptance | Technical | IEC 61701:2020 is acceptable.
16 | Part B | 181 | 1.1 | IS 16664: 2018 | Available IEC 62716:2013 for acceptance | Technical | IEC 62716:2013 is acceptable.
17 | Part B | 181 | 1.1 | IS 17210: Part 1: 2019 | Available IEC TS 62804-1:2015 for acceptance under conditions of 85°C/85% RH for minimum 96 hours | Technical | IEC TS 62804-1:2015 is acceptable with 85°C/85% RH for 192 hours.
18 | Part B | 183 | 3.2 | The Owner reserves the right to conduct Pressure Cooker (PC) test/ Highly Accelerated Stress Test (HAST) to confirm the durability of the back sheet in accelerated conditions | Test condition to be mentioned as it is not as per IEC standards | Technical | Kindly refer Amendment-1.
19 | Part B | 183 | 3.7 | Each PV Module shall be provided a RFID tag which is embedded inside the module lamination and must be able to withstand harsh environmental conditions. The RFID data | RFID tag out side the laminate and rear side of the module | Technical | Kindly refer Amendment-1.
20 | Part B | 184 | 4.2 | The modules shall be warranted for minimum of 10 years against all material/ manufacturing defects and workmanship. | Aesthetic defects not leading to performance or reliability issues are excluded | Technical | The terms and conditions of the tender document shall prevail.
21 | Part B | 184 | 5.3 | The BOM proposed shall be the subset of Constructional Data Form (CDF)s of all the test reports | Shall be subset of CDF of IEC 61215/61730 | Technical | The terms and conditions of the tender document shall prevail.
22 | Part B | 185 | 6.2 | The Owner shall perform material inspection at the Manufacturer’s factory before the start of proposed manufacturing schedule. Proof of procurement of components as per the approved BOM mentioning manufacturer name, manufacturing date and relevant test certificate shall be submitted during material inspection for verification | BOM audits can be performed in-line. It is not feasible to stock RM inventory for inspection linked to production go-aheads | Technical | Kindly refer Amendment-1.
23 | Part B | 185 | 6.3 | The Manufacturing shall start only after the clearance by the Owner after the material inspection | As above | Technical | Kindly refer Amendment-1.
24 | Part B | 185 | 6.4 | The cells used for module making shall be free from all defects like edge chipping, breakages, printing defects, discoloration of top surface etc. Only Class A solar cell shall be used. | Cells qualification for as per manufacturer's internal qualification criteria. | Technical | Acceptance criteria shall be mutually agreed during approval of PV Module post award.
25 | Part B | 185 | 6.5 | The modules shall be uniformly laminated without any lamination defects | Modules acceptance as per manufacturer's QAP | Technical | Acceptance criteria shall be mutually agreed during approval of PV Module post award.
26 | VII | 185 | 6.6 | Current binning of modules shall be employed so that current mismatch of modules in a pallet does not exceed 1% of Current at Maximum Power (Imp). Different color codes shall be provided on the modules as well as pallet for identification of different bins. Maximum three nos. of bins will be allowed. | Sorting of module on Pmax | Technical | The terms and conditions of the tender document shall prevail.
27 | VII | 187 | 6 (i) | Sampling Process Flash Test - General inspection level I Visual Inspection - General inspection level I Electroluminescence -General inspection level I | Flash - S4 2.5 Visual -S4 4 EL - S4 2.5 | Technical | The terms and conditions of the tender document shall prevail.
28 | VII | 188 | 7 | Decision Rule for acceptance / Rejection Major AQL 2.5 Minor AQL 4 | For Aesthetic defects Minor AQL 4 Major AQL 4 | Technical | The terms and conditions of the tender document shall prevail.
29 | VII | 188 | 8.1.(i) | Calibration of Sun simulator: Sun simulator shall be calibrated as per Primary Reference Module (Gold) or Secondary Reference Module (Silver). | Flasher regular verification using secondary module. In case of deviation, calibration is being done | Technical | Accepted.
30 | VII | 188 | 8.1 (ii) | All modules shall be tested at Standard Test Condition in the calibrated Sun simulator. Measured Pmax (Maximum Power) shall be with in ± 2% of Pmax measured during production | Electrical Testing at STC Conditions Pmax = Pnom ± 2% in PSI & for entire lot Pavg >Pnom | Technical | The terms and conditions of the tender document shall prevail.
31 | VII | Page 6 of 17 | 2. Technical Requirements | Cell/ Module Technology- Mono-crystalline / Thin-Film CdTe | Please accept multicrystalline technology also. As of now, domestically manufactured monocrystalline solar cells are unavailable in India. Hence request to accept multicrystalline technology also. | Technical | The terms and conditions of the tender document shall prevail.
32 | VII | Page 6 of 17 | 2. Technical Requirements | Module Efficiency ≥ 19.5% for Mono-crystalline ≥ 18.5% for Thin-film CdTe | Please include module efficiency ≥ 16.5% for Multicrystalline also | Technical | The terms and conditions of the tender document shall prevail.
33 | VII | Page 6 of 17 | 2. Technical Requirements | Temperature co-efficient of power Not less than -0.40%/°C for Mono-crystalline Not less than -0.32%/°C for Thin Film CdTe | Please include Temperature co-efficient of power Not less than -0.40%/°C for Multi-crystalline | Technical | The terms and conditions of the tender document shall prevail.
34 | VII | Page 8 of 17 | 4. Warranty | 4.3 The above warranties shall be backed by third party insurance. | The third party Insurance clause may be waived off for PSUs. | Technical | The terms and conditions of the tender document shall prevail.
35 | II | Page 9 of 47 | 10 (I) (f) | Power of Attorney for authorized signatory in non-judicial stamp paper (as per ‘Form F-19’) | BHEL is having its general Power of attorney (for participation in tenders) and the same shall be submitted by BHEL. Kindly confirm. | Contractual | All such general PoA cases shall be dealt on case to case basis. However in general such authorized GPAs are acceptable.
36 | III | Page 2 of 7 of annexure to BDS | 1.2 | The PV Module manufacturer having a manufacturing facility capacity of minimum 560 MWp/ annum if Submitting its bid for Package Capacity of 420 MWp The PV Module manufacturer having a manufacturing facility capacity of minimum 1120 MWp/ annum if Submitting its bid for Package Capacity of 840 MWp | It is requested to kinldy permit the bidders to quote who are satisfying the following criteria for giving chances for maximum number of participation. The PV Module manufacturer has a manufacturing facility capacity of 200 MW/ annum. Also, please allow Bidders/Module Suppliers to procure SPV Modules from Multiple OEMs. | Contractual | The terms and conditions of the tender document shall prevail.
37 |  |  |  | General | We kindly request to accept additional queries. | Contractual | Query not clear.
38 | VII | page 3 of 17 | 1.1 | The scope of supply includes Manufacturing, Testing, Packing and Forwarding, Transportation to Site and Unloading of domestically manufactured Solar PV Modules with domestically manufactured solar cells. | It is requested to kindly exclude the scope of Unloading from the Scope of SPV Module Supplier/Bidder and consider the scope of Unloading in the scope of SECI through its Epc Contractor. Kindly Accept. | Technical | The terms and conditions of the tender document shall prevail.
39 |  |  |  | General | If delay from scheduled completion is on account of employer, then any statutory variation beyond stipulated Delivery/ Commissioning/Completion schedule shall be to customer’s account. | Contractual | All such cases are dealt with due diligence on case to case basis.
40 | Annexure to BDS | Page 4, 5 of 7 | 1.3 | For bid of 1 package (420 MW DC): - Minimum Average Annual Turnover (MAAT) in the last three financial years (i.e. FY 2019-20, 2020-21 & 2021-22) should be INR 380 Crores (~USD 48 Mn).MAAT shall mean Revenue from Operations as incorporated in the profit & loss account excluding other income, e.g. sale of fixed assets. This has to be certified by a practicing Chartered Accountant/Statutory Auditor. - Positive net worth in last financial year to be computed as per company's act 2013. - Min working capital of INR 238 Crores (~USD 30 Mn). Bidders participating under Route 2 can use financial credentials of their Parent/ Holding/ Subsidiary/ Group company. | - The bidders parent/holding company is a foreign company listed in NASDAQ. - We request SECI to consider US GAAP based audited financial results on Calender Year basis for the qualification. - We further request SECI to not insist on CA or Statutory Auditor certifications for MAAT, Net Worth, WC etc as the financial of the foreign parent is prepared on US GAAP basis and not as per Indian accounting standards/company's act. | Finance | Audited Financials of the Bidder can be considered based on the calender year, if the calender year is followed in their country. But, a certificate from statutory Auditor or CA would be required to be submitted.
41 | GPC | Page 6 of 46 | 1.1.24 | DEFINITIONS - DRAWINGS shall include maps, plans and tracings, supporting documents, specifications or prints or sketches thereof with any modifications approved in writing by the Engineer-in-Charge/Project Manager and such other drawing as may, from time to time, be furnished by the Supplier. | As this Definition is not relevant for this RFP, we request this to be kindly removed | Contractual | Kindly refer Amendment-1.
42 | GPC | Page 7 of 46 | 1.1.29 | GUARANTEE TEST(S) means the test(s) specified in the Technical Specifications to be carried out to ascertain whether the supplies or a specified part thereof is able to attain the Functional Guarantees specified in the Technical Specifications. | As this Definition is not relevant for this RFP, we request this to be kindly removed | Contractual | Kindly refer Amendment-1.
43 | GPC | Page 7 of 46 | 1.1.32 | INSTALLATION SERVICES means all those services ancillary to the supply of the Plant and Equipment for the Facilities, to be provided by the Supplier under the Contract; e.g., transportation and provision of marine or other similar insurance (s), inspection, expediting, site preparation supply (including the provision and use of Supplier’s Equipment and the supply of all structural and supply materials required), installation including civil and allied supply etc., testing, pre-commissioning, commissioning, operations, maintenance, the provision of operations and maintenance manuals, training of Owner’s Personnel etc.. | We request SECI to limit the scope to Manufacturing, Testing, Packing and Forwarding and Transportation including Freight & Insurance and Loading at suppliers factory or warehouse. Installation services be removed from the scope. | Contractual | Kindly refer Amendment-1.
44 | GPC | Page 8 of 46 | 1.1.45 | SPECIFICATION shall mean all directions the various Technical Specifications, provisions attached and referred to the Tender Documents which pertain to the method and manner of performing the supply or supply to the quantities and qualities of the supply and the materials to be furnished under the Contract for the supply, as may be amplified or modified by the Owner or Engineer-in-Charge/Project Manager during the performance of Contract in order to provide the unforeseen conditions or in the best interests of the supply. It shall also include the latest edition of relevant Standard Specifications including all addenda/ corrigenda published before entering into Contract. | Since the modules that will be supplied in terms of this Contract will be of a specific technical specification as of the date of signing of the Contract, any changes that may change the technical specifications may limit the ability of the modules to carry out any modifications in the modules that is a single product manufactured by the Bidder, and not custom manufactured. We therefore request this amenability to be removed or it be clarified that any change will be minor in nature and will not change the technical specifications. | Technical | The terms and conditions of the tender document shall prevail.
45 | GPC | Page 8 and 33 of 46 | 1.1.50 and 53.2 | DEFECT LIABILITY PERIOD in relation to scope of work means 12 (Twelve) months from the date of delivery of modules at site during which the supplier stands responsible for rectifying all defects/ rejection that may appear in the works executed by the supplier in pursuance of the Contract and includes warranties against any defects covering all materials supplied by the supplier and works executed against workmanship defects. - 12 months period of liability from date of delivery. - Repair, replace or otherwise make good the defective supplies after consulting with Buyer. - The Defect Liability Period is the date from material delivery at site, during which the Supplier must repair/replace any defect identified by the Project Manager / EIC. All the expenses to repair the defects shall be borne by the Supplier and no additional cost charged to the Owner. - In addition, the Supplier shall also provide an extended warranty for any such component of the Facilities and for the period of time. Such obligation shall be in addition to the defect liability specified. | As this is a standard module supply contract, the Supplier warranty will more than sufficiently cover for any defects. Hence, we request SECI to kindly remove the concept of DLP from this contract. DLP is more relevant in case of EPC contracts. Acceptable defects should be as per the guidelines of Supplier warranty and user guide | Technical | The terms and conditions of the tender document shall prevail.
46 | GPC | Page 8 of 46 | 2.1 | The proposed location of Project site(s) will be updated to the supplier during the execution stage. | We request SECI to notify the details of site at least 6 months in advance of the delivery schedule | Contractual | Site location will be informed to the successful suppliers well in advance before the actual supply date.
47 | GPC | Page 8 of 46 | 2.2. | The Owner will, at his own discretion and convenience (if such surplus land is available) and for the duration of the execution of the supply make available near the site, land for supply of Supplier's Temporary Field Office, godowns and assembly yard required for the execution of the Contract. On completion of the supply undertaken by the Supplier, he shall remove all temporary work erected by him and have the Site cleaned as directed by Engineer-in-Charge/Project Manager. If the Supplier shall fail to comply with these requirements, the Owner may, at the expenses of the Supplier remove such surplus and rubbish materials and dispose off the same as he deems fit and get the site cleared as aforesaid; and Supplier shall forthwith pay the amount of all expenses so incurred and shall have no claim in respect of any such surplus materials disposed off as aforesaid. But the Owner reserves the right to ask the Supplier any time during the pendency of the Contract to vacate the land by giving 07 (Seven) day notice on security reasons or on national interest or otherwise. The Supplier shall put up temporary structures as required by them for their office and supply stores only in the area allocated to them on the project site by the Owner or his authorized representative. No tea stalls/ canteens should be put up or allowed to be put up by Supplier in the allotted land or complex area without written permission of the Owner. No unauthorized buildings, supply or structures should be put up by the Supplier anywhere on the project site. No person except for authorized watchman shall be allowed to stay in the Supplier's area after completion of the day's job without prior written intimation to Engineer-in-Charge/Project Manager | As a module only supplier, supplier will not be requiring or utilizing any land for execution of the Contract, and hence request this to be removed. | Contractual | Kindly refer Amendment-1.
48 | GPC | Page 9 of 46 | 2.3 | No Land shall be made available for residential accommodation for staff and labor of Supplier | As a module only supplier, supplier will not be requiring or utilizing any land for execution of the Contract, and hence request this to be removed. | Contractual | Kindly refer Amendment-1.
49 | GPC | Page 9 of 46 | 3.3 | The bidder should furnish, along with his Tender, details of previous experience in having successfully completed in the recent past supply of this nature, together with the names of Owners, location of sites and value of Contract, date of commencement and completion of supply, delays if any, reasons of delay and other details along with documentary evidence(s). | Since the Supplier is in the process of constructing a fully integrated green field solar module manufacturing facility in India, the bidder be allowed to produce experience of having supplied solar modules in India through its parent/ affiliate companies in the past. | Contractual | The terms and conditions of the tender document shall prevail.
50 | GPC | Page 14 of 46 | 20.1 | A list of force majeure events have been described in Section 20.1. | We request the following to be added in the definition of Force Majeure events. Any current or future pandemic (that includes Covid 19), epidemic, public health and safety emergency, quarantine, or other infectious disease outbreak that causes: (a) in the case of Owner, a delay or disruption to Owner's ability to accept delivery of Modules at the point of destination/ delivery site or perform its other obligations under the Contracts , and (b) in the case of Supplier, a disruption in production supply chains, transportation facilities or services, labor or other human resources, utility services, or other resources or services necessary for the production, delivery or storage of the Modules. For the avoidance of doubt, the Parties agree that Force Majeure does not include any event that results in new or additional costs, charges, duties, levies, tariffs or taxes that are either payable under the Contracts or, in respect of Owner only, the project into which the Modules are to be installed. | Contractual | Kindly refer Amendment-1.
51 | GPC | Page 15 and 16 | 21 and 22 | The Owner shall at its sole discretion upon reaching the maximum LD limit , as an alternative to the Liquidated Damages at its option, get supply executed from elsewhere at the risk and cost of the Supplier irrespective of the fact whether the scope of Contract is identical to the original scope of Contract and in case the Owner chooses the alternative course as mentioned, it will be entitled to recover compensation/ damages from the Supplier irrespective of maximum limit prescribed under Clause 21.1. | This is a supply only scope. If the Supplier fails to supply as per the delivery schedule, and the Owner procures modules from a third party, the compensation payable by supplier should be limited to only the differential costs for the same scope of supply of modules, and not for an expanded scope if given to the third party supplier. that will be unfair and penalizing for the Supplier if the supplier has to bear the cost for expanded scope beyond supply to the delivery site of the owner. Furthermore, we request SECI to consider excluding right of termination from the GPC in event of delay. | Contractual | The terms and conditions of the tender document shall prevail.
52 | GPC | Page 15 and 16 | 21.1 | Subject to Force Majeure Clause, if the Supplier fails to comply with the Time of Supply or any extension thereof in accordance with timelines as mentioned under the SPC, then the Supplier shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the Contract Price for the whole of the supplies as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the supplies. The Owner may, without prejudice to any other method of recovery, deduct the amount of such damages from any amount due or to become due to the Supplier. The payment or deduction of such damages shall not relieve the Supplier from his obligation to complete the Supply, or from any other of his obligations and liabilities under the Contract. Once the maximum limit is reached, Owner may consider the termination of contract and/or shall have the discretion of getting executed the supply from the Supplier with the maximum limit of Liquidated damages. Any such recovery on account of the Liquidated damages can be done from the running bills of the Supplier by Owner | We request SECI to kindly consider levy of LD only on undelivered portion of the supply based on the schedule provide by the winning bidder during Contract execution/Award | Contractual | Kindly refer Amendment-1.
53 | GPC | Page 16 of 46 | 23.1(a) | To determine the event in which the Contract shall stand terminated and shall cease to be in force and effect on and from the date appointed by the Owner on that behalf, whereupon the Supplier shall stop forthwith any of the Supplier's supply then in progress, except such supply as the Owner may, in writing, require to be done to safeguard any property or supply, or installations from damage. | This being a supply only scope, the below struck through portion may be deleted. To determine the event in which the Contract shall stand terminated and shall cease to be in force and effect on and from the date appointed by the Owner on that behalf, whereupon the Supplier shall stop forthwith any of the Supplier's supply then in progress, except such supply as the Owner may, in writing, require to be done to safeguard any property or supply, or installations from damage. | Contractual | The terms and conditions of the tender document shall prevail.
54 | GPC | Page 16 of 46 | 23.2(a) | The whole or part of the Contract Performance Security furnished by the Supplier is liable to be forfeited without prejudice to the right of the Owner to recover from the Supplier the excess cost referred to in the Clause aforesaid, the Owner shall also have the right of taking possession and utilizing in completing the supplies or any part thereof, such as materials, equipment and plants available at supply site belonging to the Supplier as may be necessary and the Supplier shall not be entitled for any compensation for use or damage to such materials, equipment and plant. | This being a supply only scope, the below struck through portion may be deleted. The whole or part of the Contract Performance Security furnished by the Supplier is liable to be forfeited without prejudice to the right of the Owner to recover from the Supplier the excess cost referred to in the Clause aforesaid, the Owner shall also have the right of taking possession and utilizing in completing the supplies or any part thereof, such as materials, equipment and plants available at supply site belonging to the Supplier as may be necessary and the Supplier shall not be entitled for any compensation for use or damage to such materials, equipment and plant. | Contractual | Kindly refer Amendment-1.
55 | GPC | Page 18 of 46 | 26.1.2 | Upon receipt of the notice of termination under GPC Sub-Clause 26.1.1, the Supplier shall either immediately or upon the date specified in the notice of termination (a) cease all further supply, except for such supply as the Owner may specify in the notice of termination for the sole purpose of protecting that part of the supplies already executed, or any supply required to leave the Site in a clean and safe condition (b) terminate all subcontracts, except those to be assigned to the Owner pursuant to paragraph (d) (ii) below (c) remove all Supplier’s Equipment from the Site, repatriate the Supplier’s and its Sub Suppliers’ personnel from the Site, remove from the Site any wreckage, rubbish and debris of any kind, and leave the whole of the Site in a clean and safe condition, and (d) subject to the payment specified in GPC Sub-Clause 26.1.3, (I) deliver to the Owner the parts of the supplies executed by the Supplier up to the date of termination (ii) to the extent legally possible, assign to the Owner all right, title and benefit of the Supplier to the supplies and to the Plant as of the date of termination, and, as may be required by the Owner, in any subcontracts concluded between the Supplier and its Sub Suppliers; and (iii) deliver to the Owner all non-proprietary drawings, specifications and other documents prepared by the Supplier or its Sub Suppliers as at the date of termination in connection with the supplies | The scope of this contract is not in nature of a EPC, hence, we request the struck off portion to be deleted. | Contractual | The terms and conditions of the tender document shall prevail.
56 | GPC | Page 18 of 46 | 26.1.3 | In the event of termination of the Contract under GPC Sub-Clause 26.1.1, the Owner shall pay to the Supplier the following amounts: (a) the Contract Price, properly attributable to the supplies executed by the Supplier as of the date of termination (b) the costs reasonably incurred by the Supplier in the removal of the Supplier’s Equipment from the Site and in the repatriation of the Supplier’s and its Sub Suppliers’ personnel (c) any amounts to be paid by the Supplier to its Sub Suppliers in connection with the termination of any subcontracts, including any cancellation charges (d) costs incurred by the Supplier in protecting the supplies and leaving the Site in a clean and safe condition pursuant to paragraph (a) of GPC Sub-Clause 26.1.2 | This being a supply only scope, the struck through portion may be deleted, as these will not apply. In the event of termination of the Contract under GPC Sub-Clause 26.1.1, the Owner shall pay to the Supplier the following amounts: (a) the Contract Price, properly attributable to the supplies executed by the Supplier as of the date of termination (b) the costs reasonably incurred by the Supplier in the removal of the Supplier’s Equipment from the Site and in the repatriation of the Supplier’s and its Sub Suppliers’ personnel (c) any amounts to be paid by the Supplier to its Sub Suppliers in connection with the termination of any subcontracts, including any cancellation charges (d) costs incurred by the Supplier in protecting the supplies and leaving the Site in a clean and safe condition pursuant to paragraph (a) of GPC Sub-Clause 26.1.2 | Contractual | The terms and conditions of the tender document shall prevail.
57 | GPC | Page 19 of 46 | 26.2.3(d) | (d) refuses or is unable to provide sufficient materials, services or labor to execute and complete the Facilities in the manner specified in the program at rates of progress that give reasonable assurance to the Owner that the Supplier can attain Completion of the Facilities by the Time for Completion as extended | We request SECI to kindly remove Section 26.2.3(d) , as this will not apply for a supply only scope. Supplier will not be executing any services at the site. | Contractual | The sufficient materials, services or labor mentioned here pertains to the logistics, transportation and unloading at site, which is in the scope of Suppllier. Hence, the terms and conditions of the tender document shall prevail.
58 | GPC | Page 20 of 46 | 26.2.4 | Upon receipt of the notice of termination under GPC Sub-Clauses 26.2.2 or 26.2.3, the Supplier shall, either immediately or upon such date as is specified in the notice of termination, (a) cease all further supply, except for such supply as the Owner may specify in the notice of termination for the sole purpose of protecting that part of the supplies already executed, or any supply required to leave the Site in a clean and safe condition (b) terminate all subcontracts, except those to be assigned to the Owner pursuant to paragraph (d) below (c) deliver to the Owner the parts of the supplies executed by the Supplier up to the date of termination (d) to the extent legally possible, assign to the Owner all right, title and benefit of the Supplier to the supplies and to the Plant as of the date of termination, and, as may be required by the Owner, in any subcontracts concluded between the Supplier and its Sub Suppliers (e) deliver to the Owner all drawings, specifications and other documents prepared by the Supplier or its Sub Suppliers as of the date of termination in connection with the supplies. | This being a supply only scope, the struck through portion may be deleted. | Contractual | The terms and conditions of the tender document shall prevail.
59 | GPC | Page 20 of 46 | 26.2.5 | The Owner may expel the Supplier, and complete the supplies itself or by employing any third Party. The Owner may, to the exclusion of any right of the Supplier over the same, take over and use with the payment of a fair rental rate to the Supplier, with all the maintenance costs to the account of the Owner and with an indemnification by the Owner for all liability including damage or injury to persons arising out of the Owner’s use of such equipment, any Supplier’s Equipment owned by the Supplier and on the Site in connection with the supplies for such reasonable period as the Owner considers expedient for the supply. | Section 26.2.5 may please be deleted as this does not apply to a supply only scope. | Contractual | Kindly refer Amendment-1.
60 | GPC | Page 20 of 46 | 26.2.6 | Subject to GPC Sub-Clause 26.2.7, the Supplier shall be entitled to be paid the Contract Price attributable to the supplies executed as of the date of termination, the value of any unused or partially used Plant on the Site, and the costs, if any, incurred in protecting the supplies and in leaving the Site in a clean and safe condition pursuant to paragraph (a) of GPC Sub-Clause 26.2.4. Any sums due the Owner from the Supplier accruing prior to the date of termination shall be deducted from the amount to be paid to the Supplier under this Contract. | Section 26.2.6 be modified as suggested below: Subject to GPC Sub-Clause 26.2.7, the Supplier shall be entitled to be paid the Contract Price attributable to the supplies executed as of the date of termination, the value of any unused or partially used Plant on the Site, and the costs, if any, incurred in protecting the supplies and in leaving the Site in a clean and safe condition pursuant to paragraph (a) of GPC Sub-Clause 26.2.4. Any sums due the Owner from the Supplier accruing prior to the date of termination shall be deducted from the amount to be paid to the Supplier under this Contract. | Contractual | The terms and conditions of the tender document shall prevail.
61 | GPC | Page 21 of 46 | 29 | The Supplier shall provide and maintain an office at the site for the accommodation of his agent and staff (With meeting room) and such office shall be open at all reasonable hours to receive instructions, notice or other communications. The Supplier shall make provisions and arrangements at site locations for temporary office (Porta cabin) including all basic amenities having electricity, furniture, Air Conditioning, Sanitation, toilet facilities, etc. at his own cost on behalf & purpose of the Owner and his staff and shall get the clearance of local authorities for setting up/supply of such facilities. Bidders are required to consider all such temporary office supply cost into his account, while bidding. These facilities shall be provided till the final handing over of the supply to the Owner. The Supplier shall ensure that the area is kept clean and sanitary conditions are maintained as laid down by the local authorities controlling the area. Further Supplier shall also provide & ensure availability of required Vehicle (Preferably SUV Segment Vehicles requiring Off Roading) with driver and fuel/Maintenance/Consumables etc. for the purpose of Mobility in and around the site for official purposes for the Owner & its staff. The vehicle as mentioned is to be provided during project supply and inspection by SECI as per requirement, failing which SECI shall have full right for alternate arrangement at the risk & cost of the Supplies | This section 29 may be please deleted as the supplier will no set up any office at site of the Owner, for a supply only scope. | Contractual | Kindly refer Amendment-1.
62 | GPC | Page 27 of 46 | 40.3 | The Supplier shall arrange for transportation, loading & unloading, local sifting, EAR insurance and safe storage of materials at project site at his own cost & risk. | Section 40.3 may please be modified as below: The Supplier shall arrange for loading, transportation and transit insurance to the Project Site of the Owner & unloading, local sifting, EAR insurance and safe storage of materials at project site at his own cost & risk. | Contractual | The provision for local shifting after delivery and EAR Insurance is removed form Contractor scope. Please refer to Amendment-1 for the same. And unloading of materials at site will be in the scope of the Supplier.
63 | GPC | Page 30 of 46 | 44.4 and 44.5 | The supplies thus procured under the scope of the contract must be kept in safe custody till put under operation, essentially free from water contact. Supplier has to ensure the appropriate and proper storage arrangement prior to the arrival of the equipment including containers, temporary structures, sheds, platforms etc. at its own cost. The Supplier shall procure and provide within the Value of Contract the whole of the materials required for the supply including steels, cement and other building materials, tools, tackles, supply plant and equipment for the completion and maintenance of the Supply except the materials which will be issued by the Owner and shall make his own arrangement for procuring such materials and for the transport thereof. The Owner may give necessary recommendation to the respective authority if so desired by the Supplier but assumes no further responsibility of any nature. The Owner will insist on the procurement of materials which bear ISI stamp and/ or which are supplied by reputed suppliers. The Supplier shall properly store all materials either issued to him or brought by him to the Site to prevent damages due to rain, wind, direct exposure to sun, etc. as also from theft, pilferage, etc. for proper and speedy execution of his supply. The Supplier shall maintain sufficient stocks of all materials required by him including commissioning spares. | We request Section 44.4 and 44.5 to be removed, since the responsibility of Supplier end when the modules are delivered at the designated delivery site of the Owner. Post that, supplier will not be able to take any obligation in respect of storage. | Contractual | Kindly refer Amendment-1.
64 | GPC | Page 31 of 46 | 50.1 and 50.2 | If, against documentary proofs, is established that any supply has been executed with unsound, imperfect supplies, or with materials of any inferior description, or that any materials or articles provided by the Supplier for the execution of the Supply are unsound, or of a quality inferior to that contracted for, or otherwise not in accordance with the Contract, the Supplier shall on demand in writing from the Engineer-in-Charge/Project Manager or his authorized representative specifying the Supply, materials or articles complained of notwithstanding that the same may have been inadvertently passed, certified and paid for, forthwith rectify or remove and reconstruct the Supply so specified and provide other proper and suitable materials or articles at his own cost. In the case of any such failure the Engineer-in-Charge/Project Manager may on expiry of notice period rectify or remove and re-execute the Supply or remove and replaced with others, the materials or articles complained of to as the case may be at the risk and expense in all respects of the Supplier. The decision of the Engineer-in-Charge/Project Manager as to any question arising under this clause shall be final and conclusive. No additional time for Project completion shall be granted for undertaking such replacement/ rectification supply by Supplier. Risk purchase Clause In the event of Suppliers failure to supply the material of acceptable quality in scheduled delivery period Owner reserves the right to procure the materials from any other source at the Suppliers risk and cost and the difference in cost shall be borne by the Supplier. Further, Owner shall retain the right of forfeiture of CPS and or any other action as deemed fit, including termination of contract, | We request that the warranty offered by the Supplier be applicable, as the supplier manufactures a single product and will not be in a position to offer different warranty claim procedure specific to this supplies. Also, we request that Section 50.2 be deleted and non compliant supplies be dealt with as per the warranty procedure. | Contractual | The terms and conditions of the tender document shall prevail.
65 | GPC | Page 32 of 46 | 51 | Subject to the provisions of sub-para (ii) of this clause, the Supplier shall, if ordered in writing by the Engineer-in-Charge/Project Manager, or his representative, temporarily suspend the Supply or any part thereof for such written order, proceed with the Supply therein ordered to be suspended until, he shall have received a written order to proceed therewith. The Supplier shall not be entitled to claim compensation for any loss or damage sustained by him by reason of temporary suspension of the Supply aforesaid. However, suitable time extension may be considered at the sole discretion of the owner., | We request that this clause be modified to provide for day for day extension in case of suspension of supplies by the Owner and a suspension be made no later than 45 days prior to the delivery schedule agreed in the contract. | Contractual | The terms and conditions of the tender document shall prevail.
66 | GPC | Page 34 of 46 and Page 35 of 46 | 54 and 55 | Entire Section 54 and 55 | Same as above, we request that the entire Section 54 and 55 be removed from the RFP | Contractual | The terms and conditions of the tender document shall prevail.
67 | GPC | Page 24 of 46 | 34.1 | The Supplier shall indemnify the Buyer against third party claims of infringement of patent, trademark or industrial design rights arising from use of goods or any part thereof in India. | SECI to clarify, as per the scope of the contract, the supplier shall indemnify against infringement related to the use of the product/ module. Any other indemnity provisions will not be applicable. | Contractual | The terms and conditions of the tender document shall prevail.
68 | GPC | Page 27 of 46 | 42 | occurrence of any of the following events pertaining to this supply only after the date seven (7) days prior to the date of Bid submission, including (i) the enactment of any new law; or (ii) an amendment, modification or repeal of an existing law; or (iii) any change in the rates of any Taxes including any duties and cess or introduction of any new tax made applicable for setting up the project. | SECI to clarify, as this seems at odds with the provisions allowed for accommodating variation in the GST rates. The change in law provision should be effective during the validity of the entire contract period (for any changes in taxes or new taxes introduced after the bid). | Contractual | The Change in Law and Regulations (clause 42 of GPC) provides amples clarity regarding any change/ variation in the Law during the course of the contract.
69 | GPC | Page 42 of 46 | 69 and 70 | - Transit/Cargo insurance for 110% of EXW value, both Supplier and Buyer to be insured for Warehouse to Warehouse + 60 days. - Comprehensive General Liability Insurance for claims arising from injuries, disabilities, disease, or death of member of public or damage to property of others due to any act or omission on the part of the Supplier, his agents, his employees, his representatives, and Sub-Supplier’s or from riots, strikes and civil commotion. | Request SECI to kindly keep the Transit insurance only up to Owner/Buyer site or warehouse and not insist for additional 60 days as storage is not in scope of supplier. Further, the entire Section 69 to be made limited to transit insurance. | Contractual | Kindly refer Amendment-1.
70 | GPC | Page 28 of 46 | 43.2.1 | The Supplier shall execute the basic and detailed design and engineering supply in compliance with the provisions of the Contract, or where not so specified, in accordance with good and sound engineering practice. | First Solar to supply module compliant to relevant certification standards and technical specifications agreed to at the time of contract. | Technical | The terms and conditions of the tender document shall prevail.
71 | GPC | Page 30 of 46 | 44.5 | The Supplier shall properly store all materials either issued to him or brought by him to the Site to prevent damages due to rain, wind, direct exposure to sun, etc. as also from theft, pilferage, etc. for proper and speedy execution of his supply. The Supplier shall maintain sufficient stocks of all materials required by him including commissioning spares. | As storage is not in scope of supplier, we request that this clause be kindly removed. | Contractual | Kindly refer Amendment-1.
72 | GPC | Page 30 of 46 | 46 | In case of any class of Supply for which there is no Specification supplied by the Owner as mentioned in the Tender Documents such Supply shall be carried out in accordance with Indian Standard Specifications and if the Indian Standard Specifications do not cover the same, the Supply should be carried out as per standard Engineering Practice subject to the approval of the Engineer-in-Charge/Project Manager. | The modules would meet only the technical speciation as per the module production specification submitted at the time of contract. The supplied modules would be certified under the relevant BIS standards and enlisted in ALMM. The scope of this contract is not in nature of a EPC, hence, we request the clause to be deleted. | Technical | The terms and conditions of the tender document shall prevail.
73 | GPC | Page 31 of 46 | 48.2 | All the tests that will be necessary in connection with the execution of the Supply as decided by the Engineer-in-Charge/Project Manager shall be carried out at the field-testing laboratory of the Owner by paying the charges as decided by the Owner from time to time. In case of non-availability of testing facility with the Owner, the required test shall be carried out at the cost of Supplier at Government or any other accredited testing laboratory. | Request SECI to Clarify the following: - Tests being discussed in this clause - if supplier needs to pay Owner for module testing by owner's test lab or 3rd party test lab. - Frequency of such testing. - In line with the standard practice of the market, we request Owner to bare the test costing at owner's or 3rd party test facility. | Technical | Kindly refer Amendment-1.
74 | GPC | Page 35 of 46 | 56 | Entire Clause 56 | SECI to clarify scope. This is not relevant for the supplier in a supply only scope. This may be please deleted, as it is not relevant | Contractual | Kindly refer Amendment-1.
75 | GPC | Page 35 of 46 | 57 | The Supplier shall provide and maintain at its own expense all lighting, fencing, watch and ward wherever necessary for the proper execution and the protection of the supply stockyard at site, or for the safety of the Owners and occupiers of adjacent property and for the safety of the public during the entire supply period. | SECI to clarify scope. This is not relevant for the supplier in a supply only scope. This may be please deleted, as it is not relevant | Contractual | Kindly refer Amendment-1.
76 | GPC | Page 35 of 46 | 58 | If during the progress of the Supply, Owner shall decide and inform in writing to the Supplier, that the Supplier has manufactured any supplies or part of the supplies unsound or imperfect or has furnished supplies inferior to the quality specified, the Supplier on receiving details of such defects or deficiencies shall at his own expenses within 07 (Seven) days of his receiving the notice, or otherwise within such time as may be reasonably necessary for making it good, proceed to alter, re- construct or remove such supply and furnish fresh equipment’s up to the standards of the specifications. In case the Supplier fails to do so, Owner may on giving the Supplier 07 (Seven) day notice in writing of his intentions to do so, proceed to remove the portion of the Supply so complained of and at the cost of Supplier's, perform all such supply or furnish all such equipment’s provided that nothing in the clause shall be deemed to deprive the Owner of or affect any rights under the Contract, the Owner may otherwise have in respect of such defects and deficiencies. | We request that the supplier's standard warranty for the modules be applied in case of any defective modules observed after supply. We request that Section 58 be deleted and replaced with Supplier's standard warranty terms | Technical | The clause talks about defectives during the progress of the supply. The terms and conditions of the tender document shall prevail.
77 | GPC | Page 36 of 46 | 59.2 | Final payment to the Supplier by the Owner will not be made. | We request that this clause be deleted as this is not clear, appearing out of context and unrelated to the provision of indemnity. | Contractual | Kindly refer Amendment-1.
78 | GPC | Page 37 of 46 | 60.5 | No exemption or reduction of Duties, Goods & Service Tax (GST) on Supply Contract quay or any port dues, transport charges, stamp duties or Central or State Government or Local Body or Municipal Taxes or from or of any other body, whatsoever, will be granted or obtained, all of which expenses shall be deemed to be included in and covered by the Schedule of Rates. The Supplier shall also obtain and pay for all permits or other privileges necessary to complete the Supply. | SECI to clarify if variation/change in GST will be allowed/reimbursed by SECI to Supplier. This has been allowed as per Clause 12.4 of the ITB (Page 12 of 47) | Finance | The clauses referred by the bidder are different and will prevail as may be applicable.
79 | GPC | Page 39 of 46 | 62 | The payment against any Lump sum item shall be made only on completion of that item (Excluding Milestones linked payment structure) as per the provision of the Contract after certification by Engineer-in-Charge/Project Manager | This may be removed and linked with the payment mechanism agreed and relevant for this contract | Finance | The terms and conditions of the tender document shall prevail.
80 | GPC | Page 39 of 46 | 63 | All running account payments shall be regarded as payment by way of advance against the final payment only and not as payments for Supply actually done and completed and shall not preclude the requiring of bad, unsound and imperfect or unskilled supply to be removed and taken away and reconstructed or re-erected or be considered as an admission of the due performance of the Contract, or any part thereof, in this respect, or of the occurring of any claim by the Supplier, nor shall it conclude, determine or affect in any way the powers of the Owner under these conditions or any of them as to the final settlement and adjustment of the accounts or otherwise, or in any other way vary or affect the Contract. The final bill shall be submitted by the Supplier within 01 (One) Month of the date of the final acceptance of the Supply; otherwise, the Engineer-in-Charge/Project Manager's measurement and of total amount payable for the Supply accordingly shall be final and binding on all parties. | This may be removed and linked with the payment mechanism agreed and relevant for this contract | Finance | The terms and conditions of the tender document shall prevail.
81 | GPC | Page 43 of 46 | 71 | Section 71 (entire) | This being a supply only scope, this clause may be removed | Contractual | The terms and conditions of the tender document shall prevail.
82 | GPC | Page 43 of 46 | 72 | Section 72 (entire) | This being a supply only scope and the supplier will not be doing any works at the site of the owner, this clause may be removed | Contractual | The terms and conditions of the tender document shall prevail.
83 | GPC, SoS and TS | Page 32 of 46, Page 8 of 17 | 53.1 (GPC), 4 (SoS and TS) | Warranty | SECI to consider warranty provisions as per the OEM/Supplier standards. SECI can issue guidance w.r.t to the tenure for workmanship and power output warranty as well as minimum warranted values for power output. However the warranty documents including the warranty process (claims, remedy etc) should be as per the Suppliers standard. | Technical | The tenure of material/manufacturing defects/workmanship warranty and power output warranty are specified in Clause 4 of Part-B of Section-VII of the tender document. Warranty document as per the Supplier's standard is acceptable as long as the relevant provisions specified in the tender document is fulfilled.
84 | SoS and TS | Page 8 of 17 | 4.3 | The above warranties shall be backed by third party insurance. | Request SECI to consider providing exemption on third party insurace for warranty incase of supplier is a public listed company with strong financial balance sheet and provisions for warranty. Request SECI to share more details on the requested third party insurance for warranty (Coverage, cap on liability, and other details). | Technical | Kindly refer Amendment-1.
85 | IFB | Page 3 of 11 | 2.8 | +/- 10% of awarded capacity | Request SECI to confirm this at least 6 months prior to the respective dispatch schedule | Contractual | If such additional +/- 10% of awarded capacity is required, it will be informed to the successful supplier at the time of placing of award.
86 | IFB | Page 3 of 11 | 2.9 | SECI has right to order additional 5% quantity at same terms with extension in delivery period | Request SECI to confirm this within 3 months from the contract award date | Contractual | The terms and conditions of the tender document shall prevail.
87 | ITB | Page 26, 27, 28 of 47 | 31.6, 31.7 | 5. Minimum decrement step for e-Auctioning is in the multiples of Rs. 5,00,00,000/- (INR Five Crores only) in the total bid value keeping the offered package capacity as constant. While applying the price reduction obtained after e-RA, all the SOR line items of the Schedule Nos 1 & 2/ SOR 1 & 2 (Module Package with Service) can be straight away reduced by applying the % reduction factor uniformly on all the line items of Schedule Nos 1 & 2/ SOR 1 & 2. And the contract will be placed on respective bidders on the reduced price accordingly. | The reduction in either Schedule 1 ( Module Price) or Schedule 2 (Packaging, Transportation, testing etc) should be as per the discretion of the Bidder as long as the bidders total price is matching the final E-RA price | Contractual | The terms and conditions of the tender document shall prevail.
88 | SoS and TS | Page 3 of 17 | A - 1 | Manufacturing, Testing, Packing and Forwarding, Supply and Transportation including Freight & Insurance including Loading, Unloading & Handling at Site | Request SECI to clarify the scope and limit to only Manufacturing, Testing, Packing, Forwarding and Transportation including Freight & Insurance and Loading at suppliers factory or warehouse. Unloading and handling at site should be under the scope of respective EPC contractor or Owner. This is standard industry practice across the solar PV industry. Also, at many places, the scope is indicated to include certain services to be performed by the Supplier towards installation which is requested to be removed from the Scope (including references to the same elsewhere in the GPC and the Contract documents) and the scope to remain limited to supply of solar modules (including freight and insurance) up to the delivery site of the Owner. | Contractual | The provision for local shifting after delivery and EAR Insurance is removed form Contractor scope. Please refer to Amendment-1 for the same. And unloading of materials at site will be in the scope of the Supplier.
89 | SoS and TS | Page 5 of 17 | B - 1 | Standards and Certification | For Thin film technology some of the certifications are not applicable. Hence request SECI to include "shall comply with the applicable" in the certifications section. | Technical | Except IS 14286: Part 1: Sec 1: 2019, all other standards are applicable for thin-film modules.
90 | SoS and TS | Page 8 of 17 | B - 5 | Approval | Unlike, the Poly/Mono silicon based cell and module manufacturers, First Solar has a fully integrated and continuous manufacturing process. Our modules are not made to specific orders or specifications of individual customers rather follow a uniform specifications with variations/improvement in nominal rating as part of production efficiency. Furthermore, the product we plan to supply for this tender is yet to be manufactured and thus we wont have the final documents like (final datasheet, test certificates etc) at the time of bidding. Considering the above, we would request SECI to reconsider the approval for module make, BOM etc. The supplier can submit the preliminary documents (datasheet, product specifications, quality plan etc) at the time of bidding and any material changes from the preliminary specifications will be informed to SECI 6 months prior to dispatch. | Technical
91 | GPC | Page 28 of 46 | 43.1 | The Supply covered under this Contract having to be executed by the Supplier on a lump-sum firm price quoted by him, the Owner will not accept any proposals for changes in Value of Contract or extension in time on account of any such changes which may arise to the Supplier's scope of Supply as a result of detailed Engineering and thereafter during the execution of Supply | SECI to clarify on "changes to the scope to supplier based on results of detailed engineering". Since, this may not be applicable for Module sale and delivery contract. This may be please deleted, as it is not relevant. | Contractual | The terms and conditions of the tender document shall prevail.
92 | SoS and TS | Page 5 of 17 | B - 1.2 | The Bidder shall submit BIS Registration Certificate of the offered PV Module in the Techno-Commercial bid. | Since the modules will be supplied for an upcoming facility, supplier cannot provide product BIS and other certifications at the time of bid submission. Request SECI to consider accepting BIS and other relevant certifications to be submitted at the time of module dispatch. | Technical | Kindly refer Amendment-1.
93 | SoS and TS | Page 6 of 17 | B - 3.1 | a laminator with a symmetrical structure, i.e., heating plate on both sides. Glass shall have transmittance above 90%. | SECI to verify the specifications at the time of Pre-dispatch inspection. | Technical | Component specifications will be verified during approval and BOM verification.
94 | SoS and TS | Page 7 of 17 | B - 3.3 | Encapsulant properties | SECI to verify the specifications at the time of Pre-dispatch inspection. | Technical | Kindly refer Amendment-1.
95 | SoS and TS | Page 7 of 17 | B - 3.4 | Sealant Properties - break down voltage (> 15 kV/mm) | SECI to verify the specifications at the time of Pre-dispatch inspection. | Technical | Component specifications will be verified during approval and BOM verification.
96 | SoS and TS | Page 7 of 17 | B - 3.5 | The module frame shall be made of anodized Aluminum. It shall have provision for earthing to connect it to the earthing grid. The anodization thickness shall not be less than 15 micron. | Proposed modules for the RFP come with Galvanized Steel Back rails. Request SECI to not limit improvements to module structure meeting the relevant IEC/ IS standards. | Technical | Kindly refer Amendment-1.
97 | SoS and TS | Page 7 of 17 | B - 3.6 | two number of IS 16781 / IEC 62852 certified MC4 compatible connectors with appropriate length of IS 17293 / IEC 62930 certified 2.5 sq.mm. or 4 sq.mm copper cable shall be provided. The cable length shall be finalized after award of the contract. | First Solar modules comes with TE PV4S connectors, First Solar recommends to use PV4S connectors to ensure compatibility. First Solar cannot comment on compatibility with connectors of different make or model. First Solar doesn’t make to order. First Solar cables come with the standard cable length as highlighted in the module product specifications. | Technical | Kindly refer Amendment-1.
98 | SoS and TS | Page 8 of 17 | B - 5.1 | with the datasheets of each component. The component datasheet shall contain all the information to substantiate the compliance for component specifications mentioned above | Certifications listed on Datasheet and supporting test reports are available on request. | Technical | It is the responsibility of the Supplier to substantiate the component specifications mentioned in the tender document with datasheet / test certificates / test reports. The terms and conditions of the tender document shall prevail.
99 | SoS and TS | Page 8 of 17 | B - 5.4 | The Supplier shall submit a detailed Manufacturing Quality Plan (MQP) for the PV Module with list of checks/tests performed during incoming material inspection, production, pre-dispatch and package. | Request SECI to accept MQP submission at the time of pre-dispatch inspection. | Technical | MQP shall be submitted at the time of approval of PV Module.
100 | SoS and TS | Page 9 of 17 | B - 6.2 | The Owner shall perform material inspection at the Manufacturer’s factory before the start of proposed manufacturing schedule. Proof of procurement of components as per the approved BOM mentioning manufacturer name, manufacturing date and relevant test certificate shall be submitted during material inspection for verification. | Unlike, the Poly/Mono silicon based cell and module manufacturers, First Solar has a fully integrated and continuous manufacturing process. Our modules are not made to specific orders or specifications of individual customers rather follow a uniform specifications with variations/improvement in nominal rating as part of production. Considering the above, we would request SECI to accept factory/ material inspection within 3 months before module dispatch, Since modules produced at the time of inspection may/ may not be delivered to SECI. All necessary documentation and proofs to be shared to SECI for review during the factory/ material inspection at the manufacturers premises only. | Technical | Material inspection shall be performed at the Manufacturer's factory during production of PV Modules. Kindly refer Amendment-1.
101 | SoS and TS | Page 9 of 17 | B - 6.6 | Current binning of modules shall be employed so that current mismatch of modules in a pallet does not exceed 1% of Current at Maximum Power (Imp). Different colour codes shall be provided on the modules as well as pallet for identification of different bins. Maximum three nos. of bins will be allowed. | Given the high current in crystalline silicon technology, current binning is performed to ensure minimal mismatch. However, thin film being a low current module technology the concept of current binning to minimize mismatch is not applicable. Request SECI to exempt this requirement for thin film module technology. | Technical | The terms and conditions of the tender document shall prevail.
102 | SoS and TS | Page11 of 17 | C - 5.2 | EL | EL inspection which is predominantly used for crystalline silicon modules to check for micro-cracks and cracks of the brittle cells laminated into module and triggering power degradation and other issues. Unlike c-Si, First Solar thin film modules do not have brittle cells and is a thin film deposition directly on glass which is flexible in nature. Thus, EL is not applicable for First Solar technology. Request SECI to exempt this requirement for thin film module technology. | Technical | The terms and conditions of the tender document shall prevail.
103 | SoS and TS | Page11 of 17 | C - 6 | Sampling Process Inspection Level General Inspection level I & S-2 | Unlike, the Poly/Mono silicon based cell and module manufacturers, First Solar has a fully integrated and continuous manufacturing process. Our modules are not made to specific orders or specifications of individual customers rather follow a uniform specifications with variations/improvement in nominal rating as part of production. Considering the above, request SECI to consider - observation of production, as per the sampling level listed in the RFP tender. - In case of re-opening of pallets, as per inspection level of Special inspection Level-3, limited to a maximum of 4 pallets. | Technical | Samples shall be representative of modules that will be supplied to SECI. The terms and conditions of the tender document shall prevail.
104 | SPC | Page 2 of 8 | 3 | The Time for Completion for the entire 1680 MWp (DC) Solar PV Module Package in total shall be 16 (Sixteen) Months from the Date of the Contract Agreement / Purchase & Service Order. PV Modules including Mandatory Spares under the award shall be supplied by the supplier in staggered deliveries during the delivery window spanning from 1st July 2023 till 31st March 2024. The above-mentioned delivery schedule is applicable for both 420 MWp package and 840 MWp package. | Request SECI to kindly modify the schedule for commencement of supply from November 2023 up to 30th June 2024 for 420 MW and up to 31st December 2024 for 840 MW. We also request SECI to allow winning bidder to provide monthly delivery schedule during the execution of the final contract/award and all penalties/LD etc to be linked with such schedule. | Contractual | Kindly refer Amendment-1.
105 | SPC | Page 2 of 8 | 3.1, 3.2, and 3.3 | Issue of Contract Agreement / Purchase & Service Order (as applicable) - Zero Date (D) Submission of GTP Datasheet, Drawing & Test Certificates - D+3 Supplies at site - D+16 | For bidders setting up new production facilities, it will be difficult to adhere to the timelines for submission of Datasheet and Test certificates. We thus request SECI to consider submission of technical documents no later than 3 months before start of supplies, and test certificates at the start of supplies. | Contractual | The terms and conditions of the tender document shall prevail.
106 | SPC and GPC | Page 3 of 8 | SPC - clause 6 and GPC - clause 25 | (d) costs incurred by the Supplier in protecting the supplies and leaving the Site in a clean and safe condition pursuant to paragraph (a) of GPC Sub-Clause 26.1.2 | CPBG should not be invoked for any defective modules related implications - defective/ damaged modules to be processed as per supplier warranty terms and procedures. | Finance | The terms and conditions of the tender document shall prevail.
107 | SPC and GPC | Page 3 of 8 | SPC - clause 6 and GPC - clause 25 | SECI can encash CPBG in case: - Any failure by supplier to comply with the requirements of any of the Obligations covered under this Tender Document and/ or Contract Agreement / Purchase & Service Order. - Failure to submit TP Datasheet, Drawing and Test certificate within 3 Mo from contract. - Failure to replace/rectify the defective PV Modules within 3 Mo from the last supply of defective modules. - In case if the percentage of defective modules crosses 10% of the total supplied modules. | SECI should consider CPS encashment only w.r.t to material breach of the contract. Further, the timelines with respect to submission of technical documents needs to be aligned with our request in the above points | Contractual | The terms and conditions of the tender document shall prevail.
108 | SPC and GPC | Page 3 of 8 | SPC - clause 6 and GPC - clause 25 | *Defective Modules : Modules found defective/damaged during the random physical/visual inspection or not having all weather worthy packing or improper palletizing or defects arising due to improper unloading. | Request SECI to consider warranty provisions as per the OEM/Supplier standards as ascertainment and remedy for Defective modules. | Contractual | The terms and conditions of the tender document shall prevail.
109 | SPC and GPC | Page 6 of 8 | SPC - clause 9 and GPC - clause 47 | - 15 days advance notice for pre-dispatch inspection by or 3rd party appointed by Buyer | Unlike, the Poly/Mono silicon based cell and module manufacturers, First Solar has a fully integrated and continuous manufacturing process. Our modules are not made to specific orders or specifications of individual customers rather follow a uniform specifications with variations/improvement in nominal rating as part of production. Considering the above, Request SECI to perform pre-dispatch inspection within 3 months before module dispatch, Since modules produced at the time of inspection may/ may not be delivered to SECI. Request SECI to provide at least 15 calender days of advance notice for any such inspections. | Contractual | The terms and conditions of the tender document shall prevail.
110 | SPC and GPC | Page 6 of 8 | SPC - clause 10 and GPC - clause 53.2 | Notwithstanding, the DLP of 12 months above, the contract shall carry a latent DLP of 5 years from date of delivery of material at site towards any defects in the modules supplied by the Supplier. | Same as our request on DLP. We request SECI to kindly remove the DLP concept from the RFP. | Contractual | The terms and conditions of the tender document shall prevail.
111 | SPC and GPC | Page 7 of 8 | SPC - clause 12 and GPC - clause 78 | - Net 30 days from acceptance of invoice by Buyers engineer in charge. For supply portion - 10% interest free advance of total contract value upon submission of CPBG, performa invoice and ABG of 100% valid uptil end of the supply term. - 60% on dispatch on pro-rate basis of supplies upon submission of invoices, GR/RR including MDCC issued by Buyers QA&I representative. - 30% on receipt of materials at site on pro-rate basis. For freight and insurance portion - 100% after successful delivery and acceptance of materials at site. | Request SECI to consider 10% advance, 80% on dispatch and 10% on receipt as payment terms for both the supply and the freight contract values. | Finance | The terms and conditions of the tender document shall prevail.
112 | IV | 27 | 40.3 | The Supplier shall arrange for transportation, loading & unloading, local sifting, EAR insurance and safe storage of materials at project site at his own cost & risk. | As per the tender doc scope is to deliver at site and site can be PAN India basis. It will be dificult to consider the freight cost. Kindly change the scope to ex works basis. Else at lest let us know the State where Modules will be delivered. | Finance | The provision for local shifting after delivery and EAR Insurance is removed form Contractor scope. Please refer to Amendment-1 for the same. And unloading of materials at site will be in the scope of the Supplier.
113 | IV | 38 | 60.7 | the Contract Value stands to be fixed inclusive of entire items, Materials, Spares, Consumables, Services and all quoted and unquoted items/ Services in the Bill of Quantity (BOQ) of the Tender/ Contract….. For Item Rate Contracts, no alteration will be allowed in the Schedule of Rates by reason of supply or any part of them being modified, altered, extended, diminished or committed. | As the suplies are starting fro July 2023 and for a 9 month suplies, it is very difficult for bidder to quote fixed price for the entire tenue. | Finance | The terms and conditions of the tender document shall prevail.
114 | IV | 35 | 56 | The term ‘Scrap’ shall refer to scrap/ waste/ remnants arising out of the unpacking of equipment, supply debris, breakage of modules, fabrication of structural steel supply and piping supply at the project site in the course of execution of the contract and shall also include any wastage of cables during the termination process while installing the cables.The Supplier shall with the agreement of the Owner promptly remove from the site any ‘Scrap’ generated during Performance of any activities at site in pursuance of the Contract. | The scope of removal of Scrap should not be with the supplier The scope is to be with the assigned EPC or SECI | Contractual | Kindly refer Amendment-1.
115 | IV | 27 | 40.3 | The Supplier shall arrange for transportation, loading & unloading, local sifting, EAR insurance and safe storage of materials at project site at his own cost & risk. | Scope like unloading, local shifting, EAR insurnce, safe storage at project should be in the scope of EPC | Contractual | The provision for local shifting after delivery and EAR Insurance is removed form Contractor scope. Please refer to Amendment-1 for the same. And unloading of materials at site will be in the scope of the Supplier.
116 | III | 3 & 4 | 1.2 & 1.3 | Bidders participating under Route II may use the financial credentials of their Parent/ Holding/ Subsidiary/ Group company for qualifying the above mentioned financial qualification requirements as per clause 1.3. However, same is not applicable for satisfying the financial qualifying requirements for bidders participating under Route I. | As per the tender doc for Route-II bidder can use finacial credentials of their parent & holding company, however under Route-I they have to use only bidding company financial. Our new facility is <1 year old and does not have the required finalcial qualification. Kindly allow Route-I bidders also to use holding/parent companys finacial credentials. Its not fair for Route-I bidders. | Finance | Kindly refer Amendment-1.
117 | VII | 5 | 1 | IS 14286: Part 1: 2019 | We can comply with BIS Current Running Guideline i.e Standard 2004 | Technical | The terms and conditions of the tender document shall prevail.
118 | VII | 5 | 1 | IS 14286: Part 1: Sec 1: 2019 | We can comply with BIS Current Running Guideline i.e Standard 2005 | Technical | The terms and conditions of the tender document shall prevail.
119 | VII | 5 | 1 | IS 14286: Part 1: Sec 2: 2019 | We can comply with BIS Current Running Guideline i.e Standard 2006 | Technical | The terms and conditions of the tender document shall prevail.
120 | VII | 5 | 1 | IS/IEC 61730-1: 2016 | We can comply with BIS Current Running Guideline i.e Standard 2007 | Technical | The terms and conditions of the tender document shall prevail.
121 | VII | 5 | 1 | IS/IEC 61730-2: 2016 | We can comply with BIS Current Running Guideline i.e Standard 2008 | Technical | The terms and conditions of the tender document shall prevail.
122 | VII | 13 | 8.4 | IS 14286: Part 2: 2019 (Insulation Test) | We can comply with BIS Current Running Guideline i.e Standard 2009 | Technical | The terms and conditions of the tender document shall prevail.
123 | VII | 13 | 8.4 | IS/IEC 61730-2: 2016 (Continuity test of equipotential bonding) | We can comply with BIS Current Running Guideline i.e Standard 2010 | Technical | The terms and conditions of the tender document shall prevail.
124 | VII | 13 | 8.4 | IS 14286: Part 2: 2019 (Wet leakage current test) | We can comply with BIS Current Running Guideline i.e Standard 2011 | Technical | The terms and conditions of the tender document shall prevail.
125 | VII | 177 | 1.1 | IS 17210: Part 1: 2019: Photovoltaic (PV) Modules - Test Methods for the Detection of Potential-Induced Degradation, Part 1: Crystalline Silicon (under conditions of 85°C/85% RH for minimum 192 hours) | As per current standard requirement it is 96 Hrs, do we need to fulfill 192 hrs compulsary | Technical | The terms and conditions of the tender document shall prevail.
126 | VII | 186 | 2 | PART – C: PRE-DISPATCH INSPECTION PROTOCOL 1) ISO 2859-1:1999 – Sampling procedures for inspection by attributes - Part 1: Sampling schemes indexed by acceptance quality limit (AQL) for lot-by-lot inspection 2) IS 14286: Part 2: 2019 – Terrestrial Photovoltaic (PV) Modules - Design Qualification and Type Approval, Part 2: Test Procedures (Second Revision) 3) IS/IEC 61730-2:2016 – Photovoltaic (PV) Module Safety Qualification, Part 1: Requirements for Construction (First Revision) | 2019 standard is still not in prevalance, we can furthur go by current Standard Running norms. | Technical | The terms and conditions of the tender document shall prevail.
127 | III | 3 & 4 | 1.2 & 1.3 | Bidders participating under Route II may use the financial credentials of their Parent/ Holding/ Subsidiary/ Group company for qualifying the above mentioned financial qualification requirements as per clause 1.3. However, same is not applicable for satisfying the financial qualifying requirements for bidders participating under Route I. | Our facility is less than 1 year old and we do not have required working capital as on date, however we can full fit this before suplies. Else pls allow us to use holding/parent companys finacial credentials. | Finance | Kindly refer Amendment-1.
128 | II | 13 | 15 | The Bids must be accompanied with 'Earnest Money Deposit (EMD)' in the form of either through NEFT/ RTGS transfer in the account of SECI or 'Demand Draft' or 'Banker's Cheque' [in favour of Solar Energy Corporation of India limited, New Delhi payable at New Delhi] or 'Bank Guarantee' as per the format given in Form F - 3 of the bidding documents. Bidders shall ensure that EMD, having a validity of at least 30 (Thirty) Days beyond the validity of the bid, must accompany the Bid in the format(s) made available in the Tender Document. In case of any extension in validity of bid, the EMD shall be extended suitably. The EMD shall be submitted in Indian Rupees only. | For EMD can you accept bid security declaration ? Or max we can provide LOC or POI from any finacial instutitions/bank | Finance | The terms and conditions of the tender document shall prevail.
129 | VII | 6 | 3 | Glass/Polymer Modules: The PV Modules glass panel shall have transmittance of above 90%. The minimum thickness of glass shall be 3.2 mm. | Kindly define what you mean by G/P. Is it transparent back sheet or backsheet | Technical | Both transparent and opaque backsheet are acceptable. The terms and conditions of the tender document shall prevail.
130 | VII | 6 | 2 | Mono-crystalline / Thin-Film CdTe | There're two set of Modules being bid here, wherein the pricing of one set overpowers the other as per industrial standards. Thus, we request you to define the Techno-commercial preference over the said sets. | Technical | No preference is provided to any specific module technology. The Bidder is free to supply any of the module technologies mentioned in the tender document. The terms and conditions of the tender document shall prevail.
131 | VII | 6 | 3 | Glass/Polymer Modules: The PV Modules glass panel shall have transmittance of above 90%. The minimum thickness of glass shall be 3.2 mm. | Kindly define the techno-commercial preference of the requested set of modules. | Technical | No preference is provided to any specific module technology/configuration. The Bidder is free to supply any of the module technologies/configurations mentioned in the tender document. The terms and conditions of the tender document shall prevail.
132 |  |  | General |  | Kindly define your prefered module wattage range. | Technical | The Supplier is free to supply any wattage as long as it meets the efficiency requirement mentioned in the tender document.
133 | V | 120 | 3.2 | Submission of GTP Datasheet, Drawing & Test Certificates | Pls accept 4 months | Technical | Kindly refer Amendment-1.
134 | V | 121 | 6 | b) In case the supplier is unable to submit GTP Datasheet, Drawing & Test Certificates within the specified deadline of 03 months from the issuance of Contract Agreement / Purchase & Service Order. | Pls accept 4 months | Technical | Kindly refer Amendment-1.
135 |  |  |  | d) In case of non-availability of same rating/wattage as of the defective PV Modules, bidder can supply higher power rating/wattage modules of the same physical dimensions for replacement. The period of replacement of defective modules shall be decided by Engineer-in-charge based on the number of failed modules and availability of mandatory spares at site. | If the SPV module supplied of wattage 550 and later due to tecnological evolution the wattage increased to 570W, does it still require to furnish all the certificates like IEC and BIS. | Technical | Yes. Replacement modules shall also comply with all standards mentioned in Clause 1 of Sectin-VII, Part-B of the tender document.
136 | V | 124 | 53.2 | Add following to the existing clause: 53.2.13 Latent Defect Liability: Notwithstanding, the defect liability period of 12 months above, the contract shall carry a latent defect liability of 5 years from date of delivery of material at site towards any defects in the modules supplied by the Supplier | Please describe Latent Defect in Brief. | Contractual | Latent Defect Liability period as defined in the tender document should be for a period of 5 years from date of delivery of material at site during which the supplier stands responsible for rectifying all defects/ rejection that may appear in the works executed by the supplier in pursuance of the Contract and includes warranties against any defects covering all materials supplied by the supplier and works executed against workmanship defects.
137 | ITB | 38 | 31.6 | (i) In case ST ≤ 1680 MWp, SE = ST – 420 MWp (ii) (ii) In case ST > 1680 MWp, SE = 1680 MWp | Kindly clarify the purpose of reducing 420 MWp in this clause,as shown below. SE = ST – 420 MWp. Concept specified & scenarios provided likely have a mismatch. Hence further explanation is requested. | Contractual | The purpose of reducing 420 MWp package (in case of ST ≤ 1680 MWp, SE = ST – 420 MWp) is to ensure competition among bidders during the e-RA process. Otherwise, if we received bids for total of 4 packages and go for awarding all 4 packages their will be no point in conducting e-RA as no one will be willing to reduce their price and as everyone is ensured of getting the package they have bid for intially. All the concept specified and the scenarios appears to be in sync.
138 | IFB | 6 | 2.8 | The Owner reserves the right to increase or decrease the quoted PV Module capacity by ± 10% at the time of placing of the order on the same price, terms and conditions of the contract. The Owner also reserves the right to order up to additional 5% of awarded PV Module capacity on the same price, terms and conditions of the contract, during the currency of the contract by giving suitable extension in delivery period for the additional quantity | a) Deletion of PO Qty should be restricted to 1% instead of 10% as entire pricing is based upon economy of scale. Deletion of PO Qty by 10% shall adversely impact such economies of scale. b) Owing to uncertainty of prices ,we would request you to delete such clause of award of additional 5% capacity at PO prices at a later date | Contractual | The terms and conditions of the tender document shall prevail.
139 | SOR | 195 | 6 | 9. Lumpsum Prices quoted by the Bidder shall include cost of any other supplies/ work(s) not specifically mentioned in the Bidding Document but necessary to make this package job complete. Quoted price is FIRM and fixed till complete execution of the entire order. Also, variation on account of Foreign Exchange rate is not to be payable extra. | We would request you to please permit uncapped price adjustment w.r.t. various global indices for Cell & BORM. Offering fixed price for such a long delivery cycle is not feasible owing to extreme uncertainty of commodity pricing across the globe. | Contractual | The terms and conditions of the tender document shall prevail.
140 | SPC | 120 | 3 | The Time for Completion for the entire 1680 MWp (DC) Solar PV Module Package in total shall be 16 (Sixteen) Months from the Date of the Contract Agreement / Purchase & Service Order. PV Modules including Mandatory Spares under the award shall be supplied by the supplier in staggered deliveries during the delivery window spanning from 1 st July 2023 till 31 st March 2024. The above-mentioned delivery schedule is applicable for both 420 MWp package and 840 MWp package. | Owner has stated both relative delivery date (16months from Award) as well as absolute delivery date (1st July’23 till 31st March’24). We understand that for all contractual purposes, relative delivery date (i.e. 16 months from award date) shall prevail as absolute delivery date in the absence of cut-off date for PO placement has no significance. Kindly confirm. | Contractual | Kindly refer Amendment-1.
141 | BDS | 64 | 6 | The bid validity period shall be 180 (One Hundred and Eighty Days) from the date of opening of Techno-Commercial Bid (Envelope-I). | As requested above, owing to high volatility in the commodity market, we would request you to kindly include price adjustment/variation clause and reduce the bid validity period to max of 90 days | Contractual | The terms and conditions of the tender document shall prevail.
142 | IFB | 14 | 6 | (i) Purchase & Service Order: For providing the Ex Works-Supply, materials including mandatory spares and any other supplies specified in the Tender Documents under the scope of Supply. And for all services i.e., including Transportation and Insurance of all supplies till site, Unloading, and Handling at Site in respect of all the supplies and any other services specified in the Contract | Unloading & handling of Modules at site by Contractor is practically not possible as the scope is restricted to Module Supply only. Hence suitable amendment is requested. | Contractual | The provision for local shifting after delivery and EAR Insurance is removed form Contractor scope. Please refer to Amendment-1 for the same. And unloading of materials at site will be in the scope of the Supplier.
143 | IFB | 12 | BIS | Rs. 19 crs , if bid submission is for 420 MWp package Rs.38 crs , if bid submission is for 840 MWp package | We would request you to kindly exempt BG inlieu of EMD and substitute the same by Bid Security declaration | Contractual | The terms and conditions of the tender document shall prevail.
144 | GPC | 89 | 25 | 3% Of Contract Value, valid for 31 months. To be furnished within 30days of placement of award. | We would request you to kindly delete the requirement of Contract Performance BG as the scope is related to Supplies only. | Contractual | The terms and conditions of the tender document shall prevail.
145 | SPC | 121 | 6 | The value of the Contract Performance Security shall be 3% (Three) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 31 Months (16 Months Project completion period) + 12 months of Defect Liability Period + 03 Months additional) from the date of its issuance. Further, any delay beyond 30 (Thirty) days in the submission of performance security shall attract interest @ 1.25% per month on the total Contract Performance Security amount, calculated on pro-rata basis accordingly. Owner at its sole discretion may cancel the Contract & forfeit 100% of EMD if applicable in case Contract Performance Security is not submitted within 45 (Forty-five) days from issuance of Contract. However, total project completion period shall remain same. Part Security shall not be accepted |  | Contractual | The terms and conditions of the tender document shall prevail.
146 | SPC | 122 | 6 | SECI at its sole discretion may encash the CPS in the following scenarios: a) In case of any default or failure of the Contractor to comply with the requirements of any of the Obligations covered under this Tender Document and/ or Contract Agreement / Purchase & Service Order shall constitute sufficient grounds for forfeiture of the entire Contract Performance Security, in such cases, the liability on account of GST will be borne by the contractor b) In case the supplier is unable to submit GTP Datasheet, Drawing & Test Certificates within the specified deadline of 03 months from the issuance of Contract Agreement / Purchase & Service Order. c) in case the supplier doesn’t replace/rectify the defective PV Modules within a time period of 3 months from the last supply of defective modules*. d) In case if the percentage of defective modules crosses 10% of the total supplied modules, irrespective of the replacements / rectification done for the defective modules. | We would request you to kindly delete the requirement of Contract Performance BG as the scope is related to Supplies only. | Contractual | The terms and conditions of the tender document shall prevail.
147 | GPC | 86 | 20.2 | A ‘Force Majeure’ means any event or circumstance or combination of events those stated below that wholly or partly prevents or unavoidably delays an Affected Party in the performance of its obligations under this Agreement, but only if and to the extent that such events or circumstances are not within the reasonable control, directly or indirectly, of the Affected Party and could not have been avoided if the Affected Party had taken reasonable care or complied with Prudent Utility Practices: • Act of God, including, but not limited to lightning, fire not caused by Suppliers’ negligence and explosion (to the extent originating from a source external to the site), earthquake, volcanic eruption, landslide, unprecedented flood, cyclone, typhoon, or tornado. {Only if it is declared / notified by the competent state / central authority / agency (as applicable)}, • Any act of war (whether declared or undeclared), invasion, armed conflict or act of foreign enemy, blockade, embargo, revolution, riot, insurrection, terrorist or military action, quarantine. • Radioactive contamination or ionizing radiation originating from a source in India or resulting from another Force Majeure Event mentioned above. 20.7 If supply is suspended by Force Majeure conditions lasting for more than two months, the Owner shall have the option of cancelling this Contract in whole or part thereof, at its discretion | 1.Force majeure should also include Pandemic/COVID-19. 2. Termination right in the event the Force Majeure exceeds 60 days should vest both with Owner & Contractor. | Contractual | Kindly refer Amendment-1.
148 | GPC | 87 | 21.1 | Subject to Force Majeure Clause, if the Supplier fails to comply with the Time of Supply or any extension thereof in accordance with timelines as mentioned under the SPC, then the Supplier shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the Contract Price for the whole of the supplies as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the supplies. Owner may consider the termination of contract and/or shall have the discretion of getting executed the supply from the Supplier with the maximum limit of Liquidated damages | Delay LD should applicable on the delayed supplies only instead of being applicable only on the entire PO value. | Contractual | Kindly refer Amendment-1.
149 | GPC | 97 | 35 | 35. Delays by Owner or his Authorized representatives 35.1 In case the Supplier's performance is delayed due to any act or omission on the part of the Owner or his authorized representatives, then the Supplier may be given due extension of time for the completion of the supply after proper due diligence by Owner, to the extent such omission on the part of the Owner has caused delay in the Supplier's performance of his supply. 35.2 No adjustment in Contract Price shall be allowed for reasons of such delays and extensions granted except as provided in Tender Document, where the Owner reserves the right to seek indulgence of Supplier to maintain the agreed Time Schedule of supply. In such an event the Supplier shall be obliged for supplying beyond stipulated supplying hours as also Sundays and Holidays and achieve the completion date of supply | Compensation, as per documented losses & damages, should be provided by Owner to Contractor for owner inflicted delays as such delays shall surely inflict losses on to Contractor owing to nature of supply value chain | Contractual | All such cases are dealt with due diligence on case to case basis.
150 | GPC | 99 | 42 | If, after the date seven (7) days prior to the date of Bid submission, any Law, Regulation, Ordinance, Order or Bye-law having the force of Law is enacted, promulgated, abrogated or changed (which shall be deemed to include any change in interpretation or application by the Competent Authorities) that subsequently affects the costs and expenses of the Supplier and/or the Time for Completion, the Contract Price shall be correspondingly increased or decreased, and/or the Time for Completion shall be reasonably adjusted to the extent that the Supplier has thereby been affected in the Performance of any of its obligations under the Contract. Supplier shall promptly and within 15 days of such enactment coming into force, forward relevant supporting documents to Owner. However, these adjustments would be restricted to direct transactions between the Owner and Supplier and Bought out items (dispatched directly from sub vendor's supply to Site). These adjustments shall not be applicable on procurement of raw materials, intermediary components, and intermediary services etc. by the Supplier. | We would request you to extend that Change in Law provision to Raw Materials as well as Module Manufacturer is reliant on entire raw material supply chain for economic feasibility of Supply Contract. | Contractual | The terms and conditions of the tender document shall prevail.
151 | GPC | 104 | 50.2 | In the event of Suppliers failure to supply the material of acceptable quality in scheduled delivery period Owner reserves the right to procure the materials from any other source at the Suppliers risk and cost and the difference in cost shall be borne by the Supplier. Further, Owner shall retain the right of forfeiture of CPS and or any other action as deemed fit, including termination of contract, | Since LD and Termination clauses are already existing hence this clause should be deleted as this seems to be duplication of other provisions. | Contractual | The terms and conditions of the tender document shall prevail.
152 | GPC | 104 | 51 | i) Subject to the provisions of sub-para (ii) of this clause, the Supplier shall, if ordered in writing by the Engineer-in-Charge/Project Manager, or his representative, temporarily suspend the Supply or any part thereof for such written order, proceed with the Supply therein ordered to be suspended until, he shall have received a written order to proceed therewith. The Supplier shall not be entitled to claim compensation for any loss or damage sustained by him by reason of temporary suspension of the Supply aforesaid. However, suitable time extension may be considered at the sole discretion of the owner., ii) In case of suspensions of entire Supply, ordered in writing by Engineer-in-Charge/Project Manager, for a period of more than 03 (Three) months, the Supplier shall have the option to terminate the Contract. | As the Employer reserves the right to suspend the contract for a period of up to 3 months, therefore such suspension should be with cost compensation to Contractor. In such a case the Module manufacturer/Contractor shall be exposed to price uncertainties in such three months period which will inflict huge losses upon Contractor. Request you to kindly consider. | Contractual | The terms and conditions of the tender document shall prevail.
153 | GPC | 106 | 56 | Disposal of Scrap The term ‘Scrap’ shall refer to scrap/ waste/ remnants arising out of the unpacking of equipment, supply debris, breakage of modules, fabrication of structural steel supply and piping supply at the project site in the course of execution of the contract and shall also include any wastage of cables during the termination process while installing the cables. The Supplier shall with the agreement of the Owner promptly remove from the site any ‘Scrap’ generated during Performance of any activities at site in pursuance of the Contract. | Scrap removal is kept in the scope of Contractor which is not feasible as Contractor shall be having no site setup to undertake such activities. Hence it is requested to delete this provision. | Contractual | Kindly refer Amendment-1.
154 | GPC | 107 | 57 | The Supplier shall provide and maintain at its own expense all lighting, fencing, watch and ward wherever necessary for the proper execution and the protection of the supply stockyard at site, or for the safety of the Owners and occupiers of adjacent property and for the safety of the public during the entire supply period. | Contractor has been envisaged to undertake watch & ward and proper lighting & fencing of stockyard at site during the entire supply period which is not feasible as Contractor shall be having no site setup to undertake such activities. Hence it is requested to delete this provision | Technical | Kindly refer Amendment-1.
155 | GPC | 90 | 26.1 | Termination for Owner’s default has not been included in specs | We would request you to include Contractor’s right for termination in case of default by Owner. | Contractual | The terms and conditions of the tender document shall prevail.
156 | GPC | 94 | 31.v | Subject to poor performance and prolonged delay of the project on account of inefficient sub-letting of the project supply, Owner may take a final decision to terminate the contract of the principal Supplier which will be binding and non-revertible and henceforth no plea in this regard shall be entertained. | Since multiple LDs & termination provisions are already existing therefore kindly delete this provision. | Contractual | The terms and conditions of the tender document shall prevail.
157 | GPC | 114 | 69.7 | All other insurance like – transit insurance (Marine/ Cargo/ others as applicable), workmen compensation, fire, third party liability, insurance against theft, Supplier’s Equipment’s, machinery breakdown policy & Environmental risk insurance of the Plant shall be in the Supplier’s scope & shall borne by the Supplier. | We understand that except for transit insurance, all other insurances are in Owner’s scope. Request you to kindly review this clause considering that Contractor shall have no site related obligation. | Contractual | Kindly refer Amendment-1.
158 | SPC | 125 | 12 | Payment shall be released within 30 days of submission and acceptance of invoice by the Engineer In Charge, having following payment milestones as mentioned below | We would request you to kindly consider payment thro’ irrevocable L/C with 30 days usance period. | Contractual | The terms and conditions of the tender document shall prevail.
159 | SPC | 126 | 12 | a) Interest free advance of 10% of the total value of Supply portion shall be released to supplier upon receipt of unconditional acceptance of Contract Agreement, detailed Performa invoice of contractor and against submission of unconditional & irrevocable Advance Bank Guarantee (ABG) with a validity period up to date of final supply amounting to 100% of total advance amount. The ABG needs to be submitted in addition to the Contract Performance Security b) ii) Sixty percent (60%) of the total value of Supply portion shall be paid upon dispatch of Solar PV Modules from manufacturer's works on pro-rata basis on production of invoices and satisfactory evidence of shipment which shall be original Goods Receipt or receipted GR/Rail Receipt including Material Dispatch Clearance c) Thirty percent (30%) payments of the total value of Supply portion shall be paid on Pro rata basis against supply, receipt and acceptance of Materials at site on submission of documents (except Advance Bank Guarantee) indicated under clause i) above, Contractor’s detailed invoice & packing list identifying contents of each shipment, evidence of dispatch (GR/ LR copy), Manufacturer’s/ Contractor’s Guarantee certificate of Quality and MDCC (Material Dispatch Clearance Certificate) issued by Owner’s authorized representative in original and Material Receipt Note (MRN | We would request you to kindly modify as under a) Advance: 20% against ABG valid till supplies are completed. This ABG shall be progressively reduced on quarterly basis. b) Against Material dispatch on pro-rata basis:80% | Contractual | The terms and conditions of the tender document shall prevail.
160 | SPC | 126 | 12 | For Freight and Insurance Portion, 100% of the payment shall be paid after successful delivery and acceptance of materials at site. Total 1000 kms have been considered as the tentative distance between the works of the bidder and Owner's site. Bidders are required to quote the unit rate on per km basis accordingly. This 1000 kms will be considered for the purpose of evaluation, however, the freight payment will be done based on the actual running km/distance of the site from the works | Pls provide price variation clause for transportation cost linked with Diesel prices as it is practically not possible for Contractor to estimate the price for entire span of deliveries owing to extreme volatility in diesel prices. | Contractual | The terms and conditions of the tender document shall prevail.

## Amendment-1
“THE MANUFACTURING, TESTING, PACKING AND FORWARDING, SUPPLY AND TRANSPORTATION OF 1680 MWP DOMESTICALLY MANUFACTURED SOLAR PV MODULES WITH DOMESTICALLY MANUFACTURED SOLAR CELLS”
Tender No : SECI/C&P/OP/11/0001/2022-23
S. No. | Section | Page No. | Clause | Original Version | Amendment
1 | Section - I (Invitation For Bids) | 4 of 11 | 2.13 | PV Modules including Mandatory Spares under the award shall be supplied by the supplier in staggered deliveries during the delivery window spanning from 1st July 2023 till 31st March 2024. | PV Modules including Mandatory Spares under the award shall be supplied by the supplier in staggered deliveries during the delivery window spanning from 1st September 2023 till 31st May 2024.
2 | Annexure of BDS Qualifying Requirements | 2 of 7 | 1.1 | The bidder should be an Indian company registered in India and may be a Group company or Holding Company or Subsidiary company of a company meeting the technical and financial eligibility requirement (s) as set forth in this section. Further, Government owned Enterprises registered and incorporated in India are also allowed to participate in this tender. However, the bidders against whom sanction/debarment/blacklisting for conducting business is imposed by Government of India, are not allowed to participate. The subsidiary of a foreign company, which is registered in India under Companies Act, 1956 or 2013 prior to the bid submission deadline, is eligible to participate. | The bidder should be an Indian company registered in India and may be a Affiliate or Holding Company or Subsidiary company of a company meeting the financial eligibility requirement (s) as set forth in this section. Further, Government owned Enterprises registered and incorporated in India are also allowed to participate in this tender. However, the bidders against whom sanction/debarment/blacklisting for conducting business is imposed by Government of India, are not allowed to participate. The subsidiary of a foreign company, which is registered in India under Companies Act, 1956 or 2013 prior to the bid submission deadline, is eligible to participate.
3 | Annexure of BDS Qualifying Requirements | 4 of 7 | 1.3.1 | Bidders participating under Route II may use the financial credentials of their Parent/ Holding/ Subsidiary/ Group company for qualifying the above mentioned financial qualification requirements as per clause 1.3. However, same is not applicable for satisfying the financial qualifying requirements for bidders participating under Route I. | Bidders participating under Route I and Route II may use the financial credentials of their Parent/ Holding/ Subsidiary/ Affiliate company for qualifying the above mentioned financial qualification requirements as per clause 1.3.
4 | Section - IV (General Purchase Conditions) | 5 of 46 | 1 | Add following to the existing clause | "SUBSIDIARY COMPANY means a company in which the Bidding Company that holds more than Fifty Percent (50%) of the paid-up equity capital directly or indirectly as the case may be.
5 | Section - IV (General Purchase Conditions) | 6 of 46 | 1.1.24 | DRAWINGS shall include maps, plans and tracings, supporting documents, specifications or prints or sketches thereof with any modifications approved in writing by the Engineer-in-Charge/Project Manager and such other drawing as may, from time to time, be furnished by the Supplier. | VOID
6 | Section - IV (General Purchase Conditions) | 7 of 46 | 1.1.29 | GUARANTEE TEST(S) means the test(s) specified in the Technical Specifications to be carried out to ascertain whether the supplies or a specified part thereof is able to attain the Functional Guarantees specified in the Technical Specifications. | VOID
7 | Section - IV (General Purchase Conditions) | 7 of 46 | 1.1.32 | INSTALLATION SERVICES means all those services ancillary to the supply of the Plant and Equipment for the Facilities, to be provided by the Supplier under the Contract; e.g., transportation and provision of marine or other similar insurance (s), inspection, expediting, site preparation supply (including the provision and use of Supplier’s Equipment and the supply of all structural and supply materials required), installation including civil and allied supply etc., testing, pre-commissioning, commissioning, operations, maintenance, the provision of operations and maintenance manuals, training of Owner’s Personnel etc.. | VOID
8 | Section - IV (General Purchase Conditions) | 8 of 46 | 2.2 | Land for Supplier’s Field Office and Godown The Owner will, at his own discretion and convenience (if such surplus land is available) and for the duration of the execution of the supply make available near the site, land for supply of Supplier's Temporary Field Office, godowns and assembly yard required for the execution of the Contract. On completion of the supply undertaken by the Supplier, he shall remove all temporary work erected by him and have the Site cleaned as directed by Engineer-in-Charge/Project Manager. If the Supplier shall fail to comply with these requirements, the Owner may, at the expenses of the Supplier remove such surplus and rubbish materials and dispose off the same as he deems fit and get the site cleared as aforesaid; and Supplier shall forthwith pay the amount of all expenses so incurred and shall have no claim in respect of any such surplus materials disposed off as aforesaid. But the Owner reserves the right to ask the Supplier any time during the pendency of the Contract to vacate the land by giving 07 (Seven) day notice on security reasons or on national interest or otherwise. The Supplier shall put up temporary structures as required by them for their office and supply stores only in the area allocated to them on the project site by the Owner or his authorized representative. No tea stalls/ canteens should be put up or allowed to be put up by Supplier in the allotted land or complex area without written permission of the Owner. No unauthorized buildings, supply or structures should be put up by the Supplier anywhere on the project site. No person except for authorized watchman shall be allowed to stay in the Supplier's area after completion of the day's job without prior written intimation to Engineer-in-Charge/Project Manager. | VOID
9 | Section - IV (General Purchase Conditions) | 9 of 46 | 2.3 | Land for Residential Accommodation No Land shall be made available for residential accommodation for staff and labour of Supplier. | VOID
10 | Section - IV (General Purchase Conditions) | 14 of 46 | 20.1 | A ‘Force Majeure’ means any event or circumstance or combination of events those stated below that wholly or partly prevents or unavoidably delays an Affected Party in the performance of its obligations under this Agreement, but only if and to the extent that such events or circumstances are not within the reasonable control, directly or indirectly, of the Affected Party and could not have been avoided if the Affected Party had taken reasonable care or complied with Prudent Utility Practices: • Act of God, including, but not limited to lightning, fire not caused by Suppliers’ negligence and explosion (to the extent originating from a source external to the site), earthquake, volcanic eruption, landslide, unprecedented flood, cyclone, typhoon, or tornado. {Only if it is declared / notified by the competent state / central authority / agency (as applicable)}, • Any act of war (whether declared or undeclared), invasion, armed conflict or act of foreign enemy, blockade, embargo, revolution, riot, insurrection, terrorist or military action, quarantine. • Radioactive contamination or ionizing radiation originating from a source in India or resulting from another Force Majeure Event mentioned above. | A ‘Force Majeure’ means any event or circumstance or combination of events those stated below that wholly or partly prevents or unavoidably delays an Affected Party in the performance of its obligations under this Agreement, but only if and to the extent that such events or circumstances are not within the reasonable control, directly or indirectly, of the Affected Party and could not have been avoided if the Affected Party had taken reasonable care or complied with Prudent Utility Practices: • Act of God, including, but not limited to lightning, fire not caused by Suppliers’ negligence and explosion (to the extent originating from a source external to the site), earthquake, volcanic eruption, landslide, unprecedented flood, cyclone, typhoon, tornado, pandemic and quarantine. {Only if it is declared / notified by the competent state / central authority / agency (as applicable)}, • Any act of war (whether declared or undeclared), invasion, armed conflict or act of foreign enemy, blockade, embargo, revolution, riot, insurrection, terrorist or military action. • Radioactive contamination or ionizing radiation originating from a source in India or resulting from another Force Majeure Event mentioned above.
11 | Section - IV (General Purchase Conditions) | 15 of 46 | 21.1 | Liquidated Damages (LD) 21.1 Subject to Force Majeure Clause, if the Supplier fails to comply with the Time of Supply or any extension thereof in accordance with timelines as mentioned under the SPC, then the Supplier shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the Contract Price for the whole of the supplies as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the supplies. The Owner may, without prejudice to any other method of recovery, deduct the amount of such damages from any amount due or to become due to the Supplier. The payment or deduction of such damages shall not relieve the Supplier from his obligation to complete the Supply, or from any other of his obligations and liabilities under the Contract. Once the maximum limit is reached, Owner may consider the termination of contract and/or shall have the discretion of getting executed the supply from the Supplier with the maximum limit of Liquidated damages. Any such recovery on account of the Liquidated damages can be done from the running bills of the Supplier by Owner. | Liquidated Damages (LD) 21.1 Subject to Force Majeure Clause, if the Supplier fails to comply with the Time of Supply or any extension thereof in accordance with timelines as mentioned under the SPC, then the Supplier shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the unexecuted value of the contract Price (corresponding to the undelivered supply) as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the supplies. The Owner may, without prejudice to any other method of recovery, deduct the amount of such damages from any amount due or to become due to the Supplier. The payment or deduction of such damages shall not relieve the Supplier from his obligation to complete the Supply, or from any other of his obligations and liabilities under the Contract. Once the maximum limit is reached, Owner may consider the termination of contract and/or shall have the discretion of getting executed the supply from the Supplier with the maximum limit of Liquidated damages. Any such recovery on account of the Liquidated damages can be done from the running bills of the Supplier by Owner.
12 | Section - IV (General Purchase Conditions) | 16 of 46 | 23.2(a) | The whole or part of the Contract Performance Security furnished by the Supplier is liable to be forfeited without prejudice to the right of the Owner to recover from the Supplier the excess cost referred to in the Clause aforesaid, the Owner shall also have the right of taking possession and utilizing in completing the supplies or any part thereof, such as materials, equipment and plants available at supply site belonging to the Supplier as may be necessary and the Supplier shall not be entitled for any compensation for use or damage to such materials, equipment and plant. | The whole or part of the Contract Performance Security furnished by the Supplier is liable to be forfeited without prejudice to the right of the Owner to recover from the Supplier the excess cost referred to in the Clause aforesaid.
13 | Section - IV (General Purchase Conditions) | 20 of 46 | 26.2.5 | The Owner may expel the Supplier, and complete the supplies itself or by employing any third Party. The Owner may, to the exclusion of any right of the Supplier over the same, take over and use with the payment of a fair rental rate to the Supplier, with all the maintenance costs to the account of the Owner and with an indemnification by the Owner for all liability including damage or injury to persons arising out of the Owner’s use of such equipment, any Supplier’s Equipment owned by the Supplier and on the Site in connection with the supplies for such reasonable period as the Owner considers expedient for the supply. | VOID
14 | Section - IV (General Purchase Conditions) | 21 of 46 | 29 | Supplier's office & Vehicle requirement for Mobility at site during supply The Supplier shall provide and maintain an office at the site for the accommodation of his agent and staff (With meeting room) and such office shall be open at all reasonable hours to receive instructions, notice or other communications. The Supplier shall make provisions and arrangements at site locations for temporary office (Portacabin) including all basic amenities having electricity, furniture, Air Conditioning, Sanitation, toilet facilities, etc. at his own cost on behalf & purpose of the Owner and his staff and shall get the clearance of local authorities for setting up/supply of such facilities. Bidders are required to consider all such temporary office supply cost into his account, while bidding. These facilities shall be provided till the final handing over of the supply to the Owner. The Supplier shall ensure that the area is kept clean and sanitary conditions are maintained as laid down by the local authorities controlling the area. Further Supplier shall also provide & ensure availability of required Vehicle (Preferably SUV Segment Vehicles requiring Off Roading) with driver and fuel/Maintenance/Consumables etc. for the purpose of Mobility in and around the site for official purposes for the Owner & its staff. The vehicle as mentioned is to be provided during project supply and inspection by SECI as per requirement, failing which SECI shall have full right for alternate arrangement at the risk & cost of the Supplier | VOID
15 | Section - IV (General Purchase Conditions) | 27 of 46 | 40.3 | The Supplier shall arrange for transportation, loading & unloading, local sifting, EAR insurance and safe storage of materials at project site at his own cost & risk. | The Supplier shall arrange for loading, transportation & unloading of materials at project site at his own cost & risk.
16 | Section - IV (General Purchase Conditions) | 30 of 46 | 44.4 | Storage of supplies The supplies thus procured under the scope of the contract must be kept in safe custody till put under operation, essentially free from water contact. Supplier has to ensure the appropriate and proper storage arrangement prior to the arrival of the equipment including containers, temporary structures, sheds, platforms etc. at its own cost. The Supplier shall procure and provide within the Value of Contract the whole of the materials required for the supply including steels, cement and other building materials, tools, tackles, supply plant and equipment for the completion and maintenance of the Supply except the materials which will be issued by the Owner and shall make his own arrangement for procuring such materials and for the transport thereof. The Owner may give necessary recommendation to the respective authority if so desired by the Supplier but assumes no further responsibility of any nature. The Owner will insist on the procurement of materials which bear ISI stamp and/ or which are supplied by reputed suppliers. | VOID
17 | Section - IV (General Purchase Conditions) | 30 of 46 | 44.5 | The Supplier shall properly store all materials either issued to him or brought by him to the Site to prevent damages due to rain, wind, direct exposure to sun, etc. as also from theft, pilferage, etc. for proper and speedy execution of his supply. The Supplier shall maintain sufficient stocks of all materials required by him including commissioning spares. | VOID
18 | Section - IV (General Purchase Conditions) | 31 of 46 | 48.2 | All the tests that will be necessary in connection with the execution of the Supply as decided by the Engineer-in-Charge/Project Manager shall be carried out at the field-testing laboratory of the Owner by paying the charges as decided by the Owner from time to time. In case of non-availability of testing facility with the Owner, the required test shall be carried out at the cost of Supplier at Government or any other accredited testing laboratory. | VOID
19 | Section - IV (General Purchase Conditions) | 31 of 46 | 48.3 | If any tests are required to be carried out in conjunction with the Supply or materials or workmanship not supplied by the Supplier, such tests shall be carried out by the Supplier and cost of such tests shall be reimbursed by the Owner. | VOID
20 | Section - IV (General Purchase Conditions) | 35 of 46 | 56 | Disposal of Scrap The term ‘Scrap’ shall refer to scrap/ waste/ remnants arising out of the unpacking of equipment, supply debris, breakage of modules, fabrication of structural steel supply and piping supply at the project site in the course of execution of the contract and shall also include any wastage of cables during the termination process while installing the cables. The Supplier shall with the agreement of the Owner promptly remove from the site any ‘Scrap’ generated during Performance of any activities at site in pursuance of the Contract. The disposal of such Scrap shall vest with the Supplier for the items supplied by the Supplier and issued by Owner under this contract for installation and supply without any additional cost to the Owner. The removal of scrap shall be subject to the due approval of Owner & Supplier producing the necessary clearance from the relevant authorities, if required by the law, in respect of disposal of the scrap. The liability for the payment of the applicable GST shall be that of the Supplier. The Supplier shall also indemnify to keep the Owner harmless from any act of omission or negligence on the part of the Supplier in following the statutory requirements with regard to removal/disposal of scrap. The undertaking shall be furnished by Supplier as per Format enclosed in the Section VI of Forms & Formats. Further, in case the laws require the Owner to take prior permission of the relevant Authorities before handing over the scrap to the Supplier, the same shall be obtained by the Supplier on behalf of the Owner. In case, the scrap is generated against the free issue material supplied by the Owner, the Supplier shall maintain a separate record of same and intimate Owner before its disposal thereafter. After due approval from Owner, the scrap should be disposed of, and its value shall be remitted to the Owner. | VOID
21 | Section - IV (General Purchase Conditions) | 35 of 46 | 57 | Watch & Ward and Lighting The Supplier shall provide and maintain at its own expense all lighting, fencing, watch and ward wherever necessary for the proper execution and the protection of the supply stockyard at site, or for the safety of the Owners and occupiers of adjacent property and for the safety of the public during the entire supply period. | VOID
22 | Section - IV (General Purchase Conditions) | 35 of 46 | 59.2 | The Supplier shall, at its own expense, defend and indemnify the Owner against all third-party claims of infringement of Intellectual Property Rights, including patent, trade mark, copy right, trade secret or industrial design rules arising from use of the products or any part thereof. The Supplier shall expeditiously extinguish any such claims and shall have full rights to defend itself there from. The Owner shall not pay any compensation to a third party resulting from such infringement and the Supplier shall be fully responsible for the same, including all expenses and court and legal fees. The Owner will give notice to the Supplier of any such claim without delay, shall provide reasonable assistance to the Supplier in disposing of the claim, and shall at no time admit any liability for or express any intent to settle the claim. Final payment to the Supplier by the Owner will not be made. | The Supplier shall, at its own expense, defend and indemnify the Owner against all third-party claims of infringement of Intellectual Property Rights, including patent, trade mark, copy right, trade secret or industrial design rules arising from use of the products or any part thereof. The Supplier shall expeditiously extinguish any such claims and shall have full rights to defend itself there from. The Owner shall not pay any compensation to a third party resulting from such infringement and the Supplier shall be fully responsible for the same, including all expenses and court and legal fees. The Owner will give notice to the Supplier of any such claim without delay, shall provide reasonable assistance to the Supplier in disposing of the claim, and shall at no time admit any liability for or express any intent to settle the claim.
23 | Section - IV (General Purchase Conditions) | 42 of 46 | 69.7 | All other insurance like – transit insurance (Marine/ Cargo/ others as applicable), workmen compensation, fire, third party liability, insurance against theft, Supplier’s Equipment’s, machinery breakdown policy & Environmental risk insurance of the Plant shall be in the Supplier’s scope & shall borne by the Supplier. | All other insurance like – transit insurance (Marine/ Cargo/ others as applicable) and workmen compensation shall be in the Supplier’s scope & shall borne by the Supplier.
24 | Section - IV (General Purchase Conditions) | 43 of 46 | 70
25 | Section - V (Special Purchase Conditions) | 2 of 8 | 3 | The Time for Completion for the entire 1680 MWp (DC) Solar PV Module Package in total shall be 16 (Sixteen) Months from the Date of the Contract Agreement / Purchase & Service Order. PV Modules including Mandatory Spares under the award shall be supplied by the supplier in staggered deliveries during the delivery window spanning from 1st July 2023 till 31st March 2024. The above-mentioned delivery schedule is applicable for both 420 MWp package and 840 MWp package. | The Time for Completion for the entire 1680 MWp (DC) Solar PV Module Package in total including Mandatory Spares under the award shall be supplied by the supplier in staggered deliveries during the delivery window spanning from 1st September 2023 till 31st May 2024. The above-mentioned delivery schedule is applicable for both 420 MWp package and 840 MWp package.
26 | Section - V (Special Purchase Conditions) | 2 of 8 | 3
27 | Section - VII (Scope of Supply & Technical Specifications) | 4 of 17 | 1.7 | PV Modules including Mandatory Spares shall be supplied from 1st July 2023 till 31st March, 2024. | PV Modules including Mandatory Spares shall be supplied from 1st September 2023 till 31st May, 2024.
28 | Section - VII (Scope of Supply & Technical Specifications) | 5 of 17 | 1.2 | PV Modules shall be registered with Bureau of India Standards (BIS) and bear the Standard Mark as per Solar Photovoltaics, Systems, Devices and Components Goods (Requirements for Compulsory Registration) Order, 2017 and subsequent amendments. The Bidder shall submit BIS Registration Certificate of the offered PV Module in the Techno-Commercial bid. | PV Modules shall be registered with Bureau of India Standards (BIS) and bear the Standard Mark as per Solar Photovoltaics, Systems, Devices and Components Goods (Requirements for Compulsory Registration) Order, 2017 and subsequent amendments.
29 | Section - VII (Scope of Supply & Technical Specifications) | 6 of 17 | 3.2 | For Crystalline Silicon Glass/Polymer PV Modules, the back sheet used in the PV modules shall be of three-layered structure durable for humid – hot conditions with properties of moisture barrier, elongation retention and UV resistance. The back sheet shall have the following properties: The Owner reserves the right to conduct Pressure Cooker (PC) test/ Highly Accelerated Stress Test (HAST) to confirm the durability of the back sheet in accelerated conditions. | For Crystalline Silicon Glass/Polymer PV Modules, the back sheet used in the PV modules shall be of three-layered structure durable for humid – hot conditions with properties of moisture barrier, elongation retention and UV resistance.
30 | Section - VII (Scope of Supply & Technical Specifications) | 7 of 17 | 3.3 | The encapsulant used for the PV modules should be UV resistant and PID resistant in nature. No yellowing of the encapsulant with prolonged exposure shall occur. The encapsulant shall have the following properties. | The encapsulant used for the PV modules should be UV resistant and PID resistant in nature. No yellowing of the encapsulant with prolonged exposure shall occur.
31 | Section - VII (Scope of Supply & Technical Specifications) | 7 of 17 | 3.5 | The module frame shall be made of anodized Aluminium. It shall have provision for earthing to connect it to the earthing grid. The anodization thickness shall not be less than 15 micron. | 3.5.1 Framed Modules The module frame shall be made of anodized Aluminium. It shall have provision for earthing to connect it to the earthing grid. The anodization thickness shall not be less than 15 micron. 3.5.2 Frameless Modules In case the offered module is frameless, the module shall be suitable for installation with retaining clamps. Alternatively, back rail may be provided for installation of modules.
32 | Section - VII (Scope of Supply & Technical Specifications) | 7 of 17 | 3.6 | The material used for junction box shall be UV resistant to avoid degradation during module life. The degree of protection of the junction box shall be at least IP 67. Minimum three number of bypass diodes (not applicable for thin-film Modules) and two number of IS 16781 / IEC 62852 certified MC4 compatible connectors with appropriate length of IS 17293 / IEC 62930 certified 2.5 sq.mm. or 4 sq.mm copper cable shall be provided. The cable length shall be finalized after award of the contract. | The material used for junction box shall be UV resistant to avoid degradation during module life. The degree of protection of the junction box shall be at least IP 67. Minimum three number of bypass diodes (not applicable for thin-film Modules) and two number of IS 16781 / IEC 62852 certified connectors with appropriate length of IS 17293 / IEC 62930 certified copper cable shall be provided.
33 | Section - VII (Scope of Supply & Technical Specifications) | 7 of 17 | 3.7 | Each PV Module shall be provided a RFID tag which is embedded inside the module lamination and must be able to withstand harsh environmental conditions. The RFID data base shall contain the following information. RFID scanner and database of all the modules containing the following information shall also be provided. ... | Each PV Module shall be provided a bar code which is embedded inside the module lamination and must be able to withstand harsh environmental conditions. Bar code scanner and database of all the modules containing serial number, technical parameters (Pmax, Voc, Isc, Vmp, Imp, Efficiency) and IV curve shall also be provided.
34 | Section - VII (Scope of Supply & Technical Specifications) | 8 of 17 | 4.3 | The above warranties shall be backed by third party insurance. | The above warranties shall be backed by third party insurance. The insurance shall cover 10% of invoice value.
35 | Section - VII (Scope of Supply & Technical Specifications) | 9 of 17 | 6.2 | The Owner shall perform material inspection at the Manufacturer’s factory before the start of proposed manufacturing schedule. Proof of procurement of components as per the approved BOM mentioning manufacturer name, manufacturing date and relevant test certificate shall be submitted during material inspection for verification. | The Owner shall perform material inspection at the Manufacturer’s factory during production of PV Modules. Proof of procurement of components as per the approved BOM mentioning manufacturer name, manufacturing date and relevant test certificate shall be submitted during material inspection for verification.
36 | Section - VII (Scope of Supply & Technical Specifications) | 9 of 17 | 6.3 | The Manufacturing shall start only after the clearance by the Owner after the material inspection. | VOID