## PAF
Annexure 9
Plant Availbility Factor Calculation Checklist
Sl. No. | Name of the Building | GPS Coordinates | Inverter Details | [11 empty] | PV Modules & String Details | [16 empty] | Main Outgoing Feeder, Transformer and Associated AC cable | [6 empty] | Plant BoS | [6 empty] | Plant Availability Factor Calculation
|  |  | Installed Inverter Details |  |  | Faulty equip detail |  | Downtime Period |  |  | Weighatge Calculation |  | Fault details |  | Installed DC capacity and string details | [8 empty] | Faulty euip detail | Downtime Period |  |  | Weightage calculation |  |  | Fault details | Faulty equip details | Downtime Period |  |  | Weightage Calculation |  | Faulty details | Faulty equip details | Downtime Period |  |  | Weightage Calculation |  | Fault details | Total Equipment downtime, hrs | (1-DFxN) x (Equipment downtime / total available generation hours of the plant) x 100 | PAF | PAF(total)
|  |  | Unit capacity of Inverter (kW) | Number of Inverters per site | Total Inverter Capacity per site (kW) | Number of Inverter unavailable | Inverter unavailble capacity (kW) | Inverter tripping time (HH:MM) | Inverter Start time (HH:MM) | Inverter downtime (Hrs) | Weightage of Each Inverter Capacity | W(inv) X number of unavailable inverters X DT(inv) | Serial No. of the faulty inverter | Reasons of Inverter tripping with Error Code | Number of Modules per Site | Unit Capacity of Module (Wp) | Plant rated DC Capacity (kWp) (Pn) | No. Modules / per string |  | No. of Strings |  | Each string capacity, Wp |  | No. of strings unavailable | PV String tripping time, (HH:MM) | PV String re-start time,(HH:MM) | PV string down time (Hrs)/day | Weightage of each PV string |  | W(pvst) X DT(pvst) | Reasons of string failure | Name of faulty euipment | Tripping / Shut down time, (HH:MM) | Plant re-start time, (HH:MM) | Plant down time hrs | Weightage | W1H1 | Reasons of failure | Details of the faulty part | Fault Start time, (HH:MM) | Fault Rectification time (HH:MM) | BoS down time hrs | Weightage | W4H4 | Reasons of failure | ∑iWiHi | (1-DFxN) x (∑iWiHi/(8760-Gout))x100 | 100-(1-DFxN) x (∑iWiHi/(8760-Gout))x100 | (Σ PAFi x Pni ) / ΣP ni
A | B | C | D | E | F = DxE | G | H=GxD | I | J | K=J -I | L=D/F | M = L x G x K | N | O | P | Q | R | S |  | Q |  | T |  | U | V | W | X = (W-V)*24 | Y= (T/1000)/R |  | Z = Y x U x X | Z' | A' | B' | C' | D'= (C' - B')*24 | E' | F'= E' x D' | G' | H' | I' | J' | K' = (J'-I')*24 | L' | M' =L' x K' | O' | P' = M+Z+F'+M' | Q' = (1-DFxN) x (P'/(8760-Gout))x100 | R'=100-Q' | S' = R' X R / ΣR
1 | Netaji Stadium | Lat: 11.6692633, Log: 92.7454682 | 27 | 3 | 81 | 0 | 0 | 0:00 | 0:00 | 0 | 0.33333 | 0 |  |  | 300 | 310 | 93 | 20 |  | 15 |  | 6200 |  | 0 | 0:00 | 0:00 | 0 | 0.066667 |  | 0 |  |  | 0:00 | 0:00 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0.2 | 0 |  | 0 | 0 | 100 | 9300
2 | Fish Aquarium | Lat: 11.671850, Log: 92.746801 | 27 | 2 | 54 | 0 | 0 | 0:00 | 0:00 | 0 | 0.5 | 0 |  |  | 200 | 310 | 62 | 18 |  | 10 |  | 5580 |  | 0 | 0:00 | 0:00 | 0 | 0.09 |  | 0 |  |  | 0:00 | 0:00 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0.2 | 0 |  | 0 | 0 | 100 | 6200
3 | Police Headquarters | Lat: 11.6738854, Log: 92.7456979 | 27 | 1 | 27 |  | 0 | 0:00 | 0:00 | 0 | 1 | 0 |  |  | 90 | 310 | 27.9 | 18 |  | 5 |  | 5580 |  | 0 | 0:00 | 0:00 | 0 | 0.2 |  | 0 |  |  | 0:00 | 0:00 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0.2 | 0 |  | 0 | 0 | 100 | 2790
4 | SP Office | Lat: 11.663821, Log: 92.741987 | 27 | 2 | 54 |  | 0 | 0:00 | 0:00 | 0 | 0.5 | 0 |  |  | 188 | 310 | 58.28 | 18 | 22 | 8 | 2 | 5580 | 6820 | 0 | 0:00 | 0:00 | 0 | 0.095745 | 0.11702 | 0 |  |  | 0:00 | 0:00 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0.2 | 0 |  | 0 | 0 | 100 | 5828
5 | JNRM college | Lat: 11.6649357, Log: 92.7513041 | 27 | 1 | 27 |  | 0 | 0:00 | 0:00 | 0 | 1 | 0 |  |  | 90 | 310 | 27.9 | 18 |  | 5 |  | 5580 |  | 0 | 0:00 | 0:00 | 0 | 0.2 |  | 0 |  |  | 0:00 | 0:00 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0.2 | 0 |  | 0 | 0 | 100 | 2790
6 | Bus Terminal, Transport Deptt | Lat: 11.6701843, Log: 92.7393136 | 27 | 2 | 54 | 0 | 0 | 0:00 | 0:00 | 0 | 0.5 | 0 |  |  | 180 | 310 | 55.8 | 18 |  | 10 |  | 5580 |  | 0 | 0:00 | 0:00 | 0 | 0.1 |  | 0 |  |  | 0:00 | 0:00 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0.2 | 0 |  | 0 | 0 | 100 | 5580
7 | Municipal Corporation | Lat: 11.6691136, Log: 92.7385455 | 27 | 4 | 108 |  | 0 | 0:00 | 0:00 | 0 | 0.25 | 0 |  |  | 352 | 310 | 109.12 | 18 | 20 | 14 | 5 | 5580 | 6200 | 0 | 0:00 | 0:00 | 0 | 0.051136 | 0.056818 | 0 |  |  | 0:00 | 0:00 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0.2 | 0 |  | 0 | 0 | 100 | 10912
8 | Secretariat | Lat: 11.6633566, Log: 92.7388821 | 27 | 1 | 27 |  | 0 | 0:00 | 0:00 | 0 | 1 | 0 |  |  | 90 | 310 | 27.9 | 18 |  | 5 |  | 5580 |  | 0 | 0:00 | 0:00 | 0 | 0.2 |  | 0 |  |  | 0:00 | 0:00 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0.2 | 0 |  | 0 | 0 | 100 | 2790
9 | Zilla Parishad | Lat: 11.6621608, Log: 92.7385555 | 27 | 2 | 54 |  | 0 | 0:00 | 0:00 | 0 | 0.5 | 0 |  |  | 194 | 310 | 60.14 | 18 |  | 10 |  | 5580 |  | 0 | 0:00 | 0:00 | 0 | 0.092784 |  | 0 |  |  | 0:00 | 0:00 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0.2 | 0 |  | 0 | 0 | 100 | 6014
10 | Polytechnic College | Lat: 11.6363335, Log: 92.7185801 | 27 | 3 | 81 |  | 0 | 0:00 | 0:00 | 0 | 0.33333 | 0 |  |  | 288 | 310 | 89.28 | 18 | 14 | 12 | 3 | 5580 | 4340 | 0 | 0:00 | 0:00 | 0 | 0.0625 | 0.048611 | 0 |  |  | 0:00 | 0:00 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0.2 | 0 |  | 0 | 0 | 100 | 8928
11 | Science Museum | Lat: 11.6550449, Log: 92.7563255 | 27 | 2 | 54 |  | 0 | 0:00 | 0:00 | 0 | 0.5 | 0 |  |  | 180 | 310 | 55.8 | 20 |  | 9 |  | 6200 |  | 1 | 0:00 | 0:00 | 0 | 0.11111 |  | 0 |  |  | 0:00 | 0:00 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0.2 | 0 |  | 0 | 0 | 100 | 5580
12 | Electricity Headquarter | Lat: 11.6734326, Log: 92.7375879 | 27 | 1 | 27 | 0 | 0 | 0:00 | 0:00 | 0 | 1 | 0 |  |  | 60 | 310 | 18.6 | 20 |  | 3 |  | 6200 |  | 0 | 0:00 | 0:00 | 0 | 0.33333 |  | 0 |  |  | 0:00 | 0:00 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0.2 | 0 |  | 0 | 0 | 100 | 1860
13 | Marine Dockyard (3 sites) | Lat: 11.6764038, Log: 92.7359699 | 27 | 12 | 324 | 0 | 0 | 0:00 | 0:00 | 8760 | 0.083333 | 0 |  |  | 1014 | 310 | 314.34 | 20 | 19 | 45 | 6 | 6200 | 5890 | 0 | 0:00 | 0:00 | 0 | 0.019724 | 0.018738 | 0 |  |  | 0:00 | 0:00 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0.2 | 0 |  | 0 | 0 | 100 | 31434
Total |  |  | 27 | 36 | 972 | 0 | 0 | [7 empty] | 3226 | 310 | 1000.06 | [28 empty] | 0 | 0 | 1300 | 100 %
Note: The above checklist is indicative only and SECI may suggest modification during execution of O&M of the plant.