## Amendment 1
Operations & Maintenance contract including Insurance for 05 (Five) Years of 10 MW Ground Mounted Solar Power Project at Badi Sid, Rajasthan Tender No SECI/C&P/OP/14/004/2022-23
S.No | Document | Page No | Clause No | Original Clause | Amendment
1 | Tender Document | 72 of 184 | Section-IV (GCC) Clause-2.5 | Land for Contractor’s Field Office, Godown and Workshop Contractor shall at his own cost arrange for a suitable premise to store his material and equipment as well as establish his office. The Owner shall also handover spares and instruments available with Owner to the contractor for safe custody and use in the projects by the contractor after taking due permission from the Owner. The contractor shall store these materials safely within the same premise. | Land for Contractor’s Field Office & Storage space / Godown The project site is equipped with Field Office and stoarge space. Same shall be handedover to the O&M contractor alongwith the spares and instruments available with Owner to the O&M contractor's for safe custody and use in the projects by the O&M contractor. After taking due permission from the Owner, the contractor shall store the spares and other materials, required for the uninteruupted Operation and maintenace of the plant, safely within the same premise. The Contractor can also set up a porta-cabin / containerised arrangement for office / storage at site if required. The Bidder is advised to visit the site and assess the requirement of space.
2 | Tender Document | 80 of 184 | Section-IV (GCC) Clause-18.1 | The contractor shall arrange office cum storage premises within 30 calendar days of issue of NOA/ LOI/WO/LOA/NTP (whichever is later). | Deleted
3 | Tender Document | 88 of 184 | Section-IV (GCC) Clause-28 | The Contractor shall provide and maintain an office near the site for the accommodation of his agent and staff (With meeting room) and such office shall be open at all reasonable hours to receive instructions, notice or other communications. Transportation of men, material, equipment, Spare etc in and around the site shall be the responsibility of the O&M Contractor. | Transportation of men, material, equipment, Spare etc in and around the site shall be the responsibility of the O&M Contractor.
4 | Tender Document | 136 of 184 | Section-V (SCC) Clause-5 | Annual Actual CUF (CUFa) shall be calculated after netting off the Auxiliary consumption and Grid outages as certified by the DISCOM and other outages not attributable to the O&M Contractor, if any, as certified by the owner Generation shortfall (Gs) in kWh: (CUFg – CUFa) X (8760 X Pac X [1-DF (N-1)]) Where, CUFg = Guaranteed CUF i.e. 21% CUF a = Actual CUF to be estimated as per Annexure -2 of SoW 8760 = refers to the number of hours in non-leap year. It shall be replaced by 8784 hours during leap year. Pac = is the plant AC capacity DF = is module degradation factor, 0.75% per year N = is the number of years of operation after operational acceptance of the Plant (Plant operation acceptance was issued on 31/03/2018.) Penalty (S) for shortfall in CUF shall be calculated as follows: i.) S1 = Generation Shortfall in kWh x 10% of PPA tariff in Rs./kWh provided the annual generation for the contract year does not fall below 15 mu or 85% of guaranteed CUF, whichever is lower. ii.) S2 = Generation Shortfall in kWh x 25% of PPA tariff in Rs./kWh provided the annual generation for the contract year is more than 10.6 mu and below 15 mu or 85% of guaranteed CUF, whichever is lower. iii.) S2 = Generation Shortfall in kWh x 100% of PPA tariff in Rs./kWh provided the annual generation for the contract year is less than 10.6 mu Thus, total penalty will be at the end of the contract year will be calculated as S total = S1+S2+S3 | Annual Actual CUF (CUFa) shall be calculated after netting off the Auxiliary consumption and Grid outages as certified by the DISCOM and other outages not attributable to the O&M Contractor, if any, as certified by the owner Generation shortfall (Gs) in kWh: (CUFg – CUFa) X (8760 X Pac X [1-DF (N-1)]) Where, CUFg = Guaranteed CUF i.e. 21% CUF a = Actual CUF to be estimated as per Annexure -2 of SoW 8760 = refers to the number of hours in non-leap year. It shall be replaced by 8784 hours during leap year. Pac = is the plant AC capacity DF = is module degradation factor, 0.75% per year N = is the number of years of operation after operational acceptance of the Plant (Plant operation acceptance was issued on 31/03/2018.) Penalty (S) for shortfall in CUF shall be calculated as follows: i.) S1 = Generation Shortfall in kWh x 10% of PPA tariff in Rs./kWh provided the annual generation for the contract year does not fall below 15 mu or 85% of guaranteed CUF, whichever is lower. ii.) S2 = Generation Shortfall in kWh x 25% of PPA tariff in Rs./kWh provided the annual generation for the contract year is more than 10.6 mu and below 15 mu or 85% of guaranteed CUF, whichever is lower. iii.) S3 = Generation Shortfall in kWh x 100% of PPA tariff in Rs./kWh provided the annual generation for the contract year is less than 10.6 mu
5 | Tender Document | 136 of 184 | Section-V (SCC) Clause-5 | Annual Actual CUF (CUFa) shall be calculated after netting off the Auxiliary consumption and Grid outages as certified by the DISCOM and other outages not attributable to the O&M Contractor, if any, as certified by the owner Generation shortfall (Gs) in kWh: (CUFg – CUFa) X (8760 X Pac X [1-DF (N-1)]) Where, CUFg = Guaranteed CUF i.e. 21% CUF a = Actual CUF to be estimated as per Annexure -2 of SoW 8760 = refers to the number of hours in non-leap year. It shall be replaced by 8784 hours during leap year. Pac = is the plant AC capacity DF = is module degradation factor, 0.75% per year N = is the number of years of operation after operational acceptance of the Plant (Plant operation acceptance was issued on 31/03/2018.) Penalty (S) for shortfall in CUF shall be calculated as follows: i.) S1 = Generation Shortfall in kWh x 10% of PPA tariff in Rs./kWh provided the annual generation for the contract year does not fall below 15 mu or 85% of guaranteed CUF, whichever is lower. ii.) S2 = Generation Shortfall in kWh x 25% of PPA tariff in Rs./kWh provided the annual generation for the contract year is more than 10.6 mu and below 15 mu or 85% of guaranteed CUF, whichever is lower. iii.) S2 = Generation Shortfall in kWh x 100% of PPA tariff in Rs./kWh provided the annual generation for the contract year is less than 10.6 mu Thus, total penalty will be at the end of the contract year will be calculated as S total = S1+S2+S3 | Monthly CUF data w.e.f. 01/04/2018 to 31/11/2022 is enclosed at Annexure 03
6 | Tender Document | 136 of 184 | Section-V (SCC) Clause-5 | 20.4 Liquidated damages during O&M period against breakdown of other Infrastructure of Plant which doesn’t affect the generation of power, directly such as but not limited to civil infrastructure, water supply system/network, other Infrastructure maintained by the Contractor as a Scope of Work for the Project (Section-VII: Scope of Works & Technical Specifications) shall be penalized @ Rs.1000/day, per incident of breakdown reported beyond 07 Days of such reporting. Cumulative value of all such LDs shall be limited to 10% of yearly O&M cost. | 20.4 Liquidated damages during O&M period against breakdown of other Infrastructure of Plant which doesn’t affect the generation of power, directly such as but not limited to civil infrastructure, water supply system/network, other Infrastructure maintained by the Contractor as a Scope of Work for the Project (Section-VII: Scope of Works & Technical Specifications) shall be penalized @ Rs.1000/day, per incident of breakdown reported beyond 07 Days of such reporting. Cumulative value of all such LDs shall be limited to 10% of total O&M contarct value.
7 | Tender Document | 7 of 26 | Section-VII | Maintenance of Water Tank, Maintenance of drainage system, rain water harvesting | Maintenance of Water Tank, Maintenance of drainage system, rain water harvesting system availbale within the plant premises.
8 | Technical Specifications | 9 of 26 | Section-VII | Contractor shall supply the Mandatory spares as per the list provided at Annexure 01 of the tender document. The mandatory spares are being procured for minimising system outage due to time required in getting replacements of defective part of equipment from the manufacturer. The contractor may use the mandatory spare available at site for replacing defective part of equipment for minimising system outage temporarily and top-up the quantity of mandatory spares so that the required quantity of mandatory spares as mentioned in Schedule of Rates (SOR) shall be made available at site at all the times. | Contractor shall supply the Mandatory spares as per the list provided at Annexure 01 of the tender document. The mandatory spares are being procured for minimising system outage due to time required in getting replacements of defective part of equipment from the manufacturer. The contractor may use spares, ,(if any) available at site with the permission of owner for replacing defective part of equipment for minimising system outage temporarily and top-up the quantity of the same spares within a period of 3 months from consumption of the borrowed spare part. However, contractor shall maintain the required qunatity of mandatory spares supplied by them at all time so that same as mentioned in Schedule of Rates (SOR) shall be made available at site at all the times.
9 | Technical Specifications | 14 of 26 | Section-VII | Arrangement of vehicle for conveyance of resources / manpower, material, and equipment shall be in the scope of contractor. SECI shall not provide any accommodation /Transportation for the employees of vendor. Everything has to be arranged by the contractor for his employees. | Arrangement of vehicle for conveyance of resources, manpower (contractor's & Owner's), material, and equipment shall be in the scope of contractor. SECI shall not provide any accommodation /Transportation for the employees of vendor. Everything has to be arranged by the contractor for his employees. It may be noted that the vehicle specified in the scope of the contract for use of SECI shall be available at all tmes for SECI's use. However, the Contractor may use it with permission of SECI's plant manager if the vehicle is available.
10 | Technical Specifications | 17 of 26 | Section-VII (clause B(p)(b)) | AMC: Contractor shall enter into AMC contract with the OEM for the following items to cover requirements of maintenance and repairs. 1) Inverters 2) Inverter transformers 3) 33KV circuit breaker 4) 33KV instrument transformers (all CTs and VTs) 5) All types of meters and relays installed at 33KV level 6) SCADA 7) Transformers 8) Any other equipment as per plant requirement The Employer shall maintain spares of major components. Spare stock of MCBs, MCCBs, fuses, lamps, indication lamps, indicating meters, terminals, wires, etc shall be | AMC: Contractor shall enter into AMC contract with the OEM for the following items to cover requirements of maintenance and repairs. 1) 33KV vacumm circuit breaker 2) SCADA 3) Transformers 4) MP control (Telemetry data communication) 5) Any other equipment as per plant requirement Make and model details are given at Annexure 4 of Amendment 01 The Employer shall maintain AMC of Inverter exclduing consumbales of the same. For inverters, the O&M contractor shall coordinate with the OEM for services under the AMC on behalf of the Employer. All type of mandatory spares as per Annexure 01 and consumables such as ( but not limited to) spare stock of MCBs, MCCBs, fuses, lamps, indication lamps, indicating meters, terminals, wires, etc shall be maintained by the O&M Contractor as per requirement for the uninterrupted O&M of the Plant. Employer shall provide SPV Module to replace the damged module. Around 100 SPV modules will be available at site.
11 | Technical Specifications |  | Section-VII | Annexure 2: Power Plant Performance & Guaranteed Generation | Annexure 2 of Amendment : Power Plant Performance & Guaranteed Generation
12 | Technical Specifications |  | Section-VII (Clause B(a)(j) | Supply of all spares, consumables and fixing / application as required as per Annexure 01 | Supply of all mandatory spares as per Annexure 01, all type of consumables and fixing / application as required for uninterrupted O&M of the plant.

## Pre Bid Clarifications
Operations & Maintenance contract including Insurance for 05 (Five) Years of 10 MW Ground Mounted Solar Power Project at Badi Sid, Rajasthan Tender No SECI/C&P/OP/14/004/2022-23
S.No | Document | Page No | Clause No | Original Clause | Bidder Query | Clarification
1 | Tender Document | 72 of 184 | Section-IV (GCC) Clause-2.3 | Water Supply to the facilities Contractor will have to make his own arrangements for supply of water for cleaning of modules and other functions required to complete the requirements mentioned in the scope of Work. The water quality should be suitable for use in this works | Please Clarify, whether Module Cleaning System is available at Site or Contractor has to do Tanker Based PV Module Cleaning | Module cleaning system is available at site. However, water shall be arranged by the contractor as per the requirement of the project. Currently Water tankers are being arranged at site by the existing O&M contractor and water is stored in the underground storage tanks available at site. 3 Nos. of Under gorund tanks are available each at MCR, LCR 1 and LCR 2. Contractor may visit the site for more information.
2 | Tender Document | 72 of 184 | Section-IV (GCC) Clause-2.5 | Land for Contractor’s Field Office, Godown and Workshop Contractor shall at his own cost arrange for a suitable premise to store his material and equipment as well as establish his office. The Owner shall also handover spares and instruments available with Owner to the contractor for safe custody and use in the projects by the contractor after taking due permission from the Owner. The contractor shall store these materials safely within the same premise. | Since the Plant is operational for O&M activity, O&M Contractor request Owner (SECI) to provide Premises for Personnel's Sitting arrangement & Store room at Solar Plant Site. Or if it is already available at site, O&M Contractor shall use the same. Please Confirm. | Refer Amendment 01
3 | Tender Document | 80 of 184 | Section-IV (GCC) Clause-18.1 | The contractor shall arrange office cum storage premises within 30 calendar days of issue of NOA/ LOI/WO/LOA/NTP (whichever is later). |  | Refer Amendment 01
4 | Tender Document | 85 of 184 | Section-IV (GCC) Clause-25.1.2 | Upon receipt of the notice of termination under GCC Sub-Clause 25.1.1, the Supplier shall either immediately or upon the date specified in the notice of termination | Request you to kindly change the duration of Temination notice to a minimum of 30 Days | The terms and conditions of the tender document shall prevail.
5 | Tender Document | 88 of 184 | Section-IV (GCC) Clause-28 | The Contractor shall provide and maintain an office near the site for the accommodation of his agent and staff (With meeting room) and such office shall be open at all reasonable hours to receive instructions, notice or other communications. Transportation of men, material, equipment, Spare etc in and around the site shall be the responsibility of the O&M Contractor. | Since the Plant is operational for O&M activity, O&M Contractor request Owner (SECI) to provide Premises for Personnel's Sitting arrangement & Store room at Solar Plant Site. Or if it is already available at site, O&M Contractor shall use the same. Please Confirm. | Refer Amendment 01
6 | Tender Document | 94 of 184 | Section-IV (GCC) Clause-37.1 | If, at any time there should be evidence or any lien or claim for which the Owner might have become liable and which is chargeable to the Contractor, the Owner shall have the right to retain out of any payment then due or thereafter to become due an amount sufficient to completely indemnify the Owner against such lien or claim and if such lien or claim be valid, the Owner may pay and discharge the same and deduct the amount so paid from any money which may be or may become due and payable to the Contractor. If any lien or claim remain unsettled after all payments are made, the Contractor shall refund or pay to the Owner all money that the latter may be compelled to pay in discharging such lien or claim including all costs and reasonable expenses. Owner reserves the right to do the same. | The Contractor's Liability should not be greater than 100% of Annual O&M Contract Value | The terms and conditions of the tender document shall prevail.
7 | Tender Document | 100 of 184 | Section-IV (GCC) Clause-51 | Change in LAW However, any increase in the rate of these taxes, duties and levies beyond the contractual completion period shall be to Contractor's account and any decrease shall be passed on to Owner. However, Change in Law shall not include (i) any change in taxes on corporate income or (ii) any change in any withholding tax on income or dividends distributed to the shareholders of the Contractor, or (iii) any change on account of regulatory measures by the Appropriate Commission. | Change is LAW should be applicable in entirety & not on conditional basis which may affect contractor in negative cashflows. As these Change in LAW are not in anyone's (Neither Owner not Contractor) Control, we request to make it applicable in entirety | The terms and conditions of the tender document shall prevail.
8 | Tender Document | 136 of 184 | Section-V (SCC) Clause-5 | Annual Actual CUF (CUFa) shall be calculated after netting off the Auxiliary consumption and Grid outages as certified by the DISCOM and other outages not attributable to the O&M Contractor, if any, as certified by the owner Generation shortfall (Gs) in kWh: (CUFg – CUFa) X (8760 X Pac X [1-DF (N-1)]) Where, CUFg = Guaranteed CUF i.e. 21% CUF a = Actual CUF to be estimated as per Annexure -2 of SoW 8760 = refers to the number of hours in non-leap year. It shall be replaced by 8784 hours during leap year. Pac = is the plant AC capacity DF = is module degradation factor, 0.75% per year N = is the number of years of operation after operational acceptance of the Plant (Plant operation acceptance was issued on 31/03/2018.) Penalty (S) for shortfall in CUF shall be calculated as follows: i.) S1 = Generation Shortfall in kWh x 10% of PPA tariff in Rs./kWh provided the annual generation for the contract year does not fall below 15 mu or 85% of guaranteed CUF, whichever is lower. ii.) S2 = Generation Shortfall in kWh x 25% of PPA tariff in Rs./kWh provided the annual generation for the contract year is more than 10.6 mu and below 15 mu or 85% of guaranteed CUF, whichever is lower. iii.) S2 = Generation Shortfall in kWh x 100% of PPA tariff in Rs./kWh provided the annual generation for the contract year is less than 10.6 mu Thus, total penalty will be at the end of the contract year will be calculated as S total = S1+S2+S3 | Annual Guaranteed CUF is 21%. We request SECI to share the Past DGR Data to understand the plant performance enabling us for foresee the CUF in coming years. | Refer Amendment 01
9 | Tender Document | 136 of 184 | Section-V (SCC) Clause-5 | 20.4 Liquidated damages during O&M period against breakdown of other Infrastructure of Plant which doesn’t affect the generation of power, directly such as but not limited to civil infrastructure, water supply system/network, other Infrastructure maintained by the Contractor as a Scope of Work for the Project (Section-VII: Scope of Works & Technical Specifications) shall be penalized @ Rs.1000/day, per incident of breakdown reported beyond 07 Days of such reporting. Cumulative value of all such LDs shall be limited to 10% of yearly O&M cost. | We understand that the Cumulative Value of LD by all means shall be limited to 10% of the Yearly O&M Contract Value | Refer Amendment 01
10 | Tender Document | 137 of 184 | Section-V (SCC) Clause-5 | The value of the Contract Performance Security shall be 3% (Three) of the Contract Value (i.e., O&M Contract). This Performance security will be valid for a total period of 63 months [60 (Sixty) months of O&M and 03 (Three) additional Months] from the date of its issuance. Envisaging the difficulty in obtaining the longer tenure of CPS in the form of BG, the successful bidder can submit Contract Performance Security in the form of Bank Guarantee (including e - Bank Guarantee) with initial validity period of 36 Months and the same may be extended for the balance period or further 36 months, within 60 days of expiry of the original CPS. | We request SECI for a CPS to be submitted as per following methodology: 1) 50% of the required CPS including the EMD, should be paid before start of the work. 2) Balance of the CPS can be collected by deducting10% of the gross amount progressively from each of the running bills of the Contractor till the total amount of the required COntract Performance Security (CPS) is collected. | The terms and conditions of the tender document shall prevail.
11 | Tender Document | 139 of 184 | Section-V (SCC) Clause-5 | Operation and Maintenance of the entire Project payment will be released on quarterly basis at the end of every quarter for each year till 05 (Five) years. | We understood the payment Term is Quarterly basis. We request you to amend the requirements wrt supporting documents, as the below process will help the O&M Contractor to have healthier cash flow in the system. Say invoice cycle is April to June month and invoice is raised on 1st July, supporting documents will be submitted for April and May months In the next billing cycle - July to Sep month ; supporting docs for June July & Aug Months will be provided. Inference - there will be a backlog of one month for which the supporting docs to be provided | The terms and conditions of the tender document shall prevail.
12 | Tender Document | 3 of 26 | Section-VII | Co-ordination with STU/SLDC/other statutory organizations as per the requirement on behalf of Employer for Joint Metering Report (JMR). | Only Coordination will be in Contractor's Scope & Payment to STU/SLDC/Other Statutory Organizations will be in the scope of Owner. Please Confirm. | All the statutory payment shall be borne by Employer on reimbursement basis upon submission of valid Payment recipt (proof of payment) by the O&M contractor.
13 | Technical Specifications | 4 of 26 | Section-VII | The contractor shall make his own arrangements for sourcing of water for cleaning of modules and other requirements in the plant. | Whether Module Cleaning System is installed at Site or O&M Contractor has to do Tanker based Cleaning | Module cleaning system is available at site. However, water shall be arranged by the contractor as per the requirement of the project. Currently Water tankers are being arranged at site by the existing O&M contractor and water is stored in the underground storage tanks available at site. 3 Nos. of Under gorund tanks are available each at MCR, LCR 1 and LCR 2. Contractor may visit the site for more information.
14 | Technical Specifications | 4 of 26 | Section-VII | Corrective and preventive O&M of the Solar Photovoltaic Power Plant including supply of spares, consumables, wear and tear, overhauling, replacement of damaged modules, invertors, PCU’s and insurance for his man, material and equipment as required, for a period covering the period of contract and one more year commencing from the date of start of O&M of the project. | Please share the list of spares which will be supplied by Owner to O&M Contractor | Please refer Annexure 01 of SoW
15 | Technical Specifications | 7 of 26 | Section-VII | Necessary intervention to SLDC & QCA shall be provided. | Please confirm the scope of Payment to SLDC which is generally taken care by Owner | All the statutory payment shall be borne by Employer on reimbursement basis upon submission of valid Payment recipt (proof of payment) by the O&M contractor.
16 | Technical Specifications | 7 of 26 | Section-VII | Maintenance of Water Tank, Maintenance of drainage system, rain water harvesting | Contractor can maintain the existing drains in the solar plant but shall not be responsible for any damage due to flooding in plant since drains are designed at the project stage and Contractor shall not be responsible for any flooding or damage to plant due to blockage or faulty design or force majeure reasons. The clause to be rephrased and contractors responsibility shall only be restricted to maintaining the drains with in plant only. Any temporary drain works undertaken to mitigate such cases by the contractor to be paid extra by the Employer Is Water Tank Available at Site. If Yes, then what is the capacity of Tank | Refer Amendment 01
17 | Technical Specifications | 8 of 26 | Section-VII | Sowing new plants, maintaining existing plants at site | O&M Contractor will lookafter existing Plants at Site. However New Vegetation/Plantation should be excluded from the O&M Contractor's Scope | The terms and conditions of the tender document shall prevail.
18 | Technical Specifications | 9 of 26 | Section-VII | Contractor shall supply the Mandatory spares as per the list provided at Annexure 01 of the tender document. The mandatory spares are being procured for minimising system outage due to time required in getting replacements of defective part of equipment from the manufacturer. The contractor may use the mandatory spare available at site for replacing defective part of equipment for minimising system outage temporarily and top-up the quantity of mandatory spares so that the required quantity of mandatory spares as mentioned in Schedule of Rates (SOR) shall be made available at site at all the times. | Given Clause is Contradictory. Please clarify whether Mandatory Spares are available at Site or Contractor has to purchase the Mandatory Spares. Further, If contractor has to purchase the mandatory spares, whether contractor is allowed to take back the unused Spares. | Refer Amendment 01
19 | Technical Specifications | 11 of 26 | Section-VII | The Contractor shall be responsible for maintaining all safety measures at the site to avoid accidents to his or his sub-contractor or SECI's Workmen. SECI’s EHS plan is attached for implementation. | EHS Plan Missing. Please share. | Plant is certified with ISO 9001:2015, 14001:2015 and 45001:2018. Therefore the contractor will be required to follow specified quality, environment, and occupational hazard and safety norms. SECI HSE requirements are attached at Annexure 05
20 | Technical Specifications | 11 of 26 | Section-VII | Contractor shall be responsible to comply with all applicable National and International Standards as well as local statutory provisions related to Environmental Protection Regulations, Health and Safety requirement | Contractor request to set the National Standards for compliance. | The terms and conditions of the tender document shall prevail.
21 | Technical Specifications | 11 of 26 | Section-VII | Contractor will ensure that O&M is being carried out by a licensed Electrician/Supervisor. A test certificate is to be produced to the ENGINEER-INCHARGE for his approva | We understand that Electrician / Supervisor License is required of Site-In-Charge of Contractor | The O&M team will have atleast one licensed Electrician / Supervisor for performing the O&M services
22 | Technical Specifications | 11 of 26 | Section-VII | It shall be the responsibility of the contractor to keep, restore, or improve every facility of the buildings, Materials (Office infrastructure such as Computer, Printer, AC, exhaust fan etc, Peripheral lights) including Housekeeping and cleaning of office, storage and all buildings. | We understand that the Computer for day to day activity will be provided by owner | Site is equipped with two desktop computers. The O&M contrator shall provide adequate infrastruture / Laptops/Computers to his manpower deputed at 10 MW badi sid project site.
23 | Technical Specifications | 12 of 26 | Section-VII | Rajasthan State Load Despatch Centre (SLDC) has nominated a Qualified Coordinating Agency (QCA) at the Pooling Substation Level for operating the Deviation Settlement mechanism (In accordance with the Deviation Settlement Mechanism Regulations, as applicable) at the Pooling station level (220KV GSS Badi Sid). The Contractor shall be responsible for carrying out the forecasting and scheduling of the energy generation from the plant facility and coordinating with the QCA for incorporating the same in the generation schedule of the GSS prepared by the QCA. Scheduling given by the Contractor shall be such that no penalty is levied on the Employer due to any deviation of actual generation from scheduling beyond the allowed limit. If any penalty is imposed on the Employer due to such deviations beyond allowed limit the same shall be passed on to the Contractor and the recovery of the same will be done from the O&M Price payable to the Contractor | Since QCA is already appointed. Please confirm whether payment to SLDC will be paid by QCA/Owner | QCA shall be appointed by the O&M contractor for facilitating energy scheduling and forecasting as per the DSM guidelines of CERC/SERC. The penalty, if any, imposed by SLDC due to DSM charges shall be paid by the O&M contractor through QCA to SLDC.
24 | Technical Specifications | 13 of 26 | Section-VII | Security staff (including one Gunman) (all through the day) | We understand that 10 Nos of Security Guards will deployed during the course of 24 Hours. For Ex: Shift A: 3 Nos Shift B: 3 Nos Shift C: 4 Nos Please Confirm our Understanding | Yes, However, the number of staff per shift may vary depending upon the site requirement.
25 | Technical Specifications | 14 of 26 | Section-VII | c) Carrying out SCADA &WMS O&M and coordinate with OEMs for AMC and as per the operational requirements | Please confirm the Scope of AMC for SCADA | Please refer SoW of the tender
26 | Technical Specifications | 14 of 26 | Section-VII | Arrangement of vehicle for conveyance of resources / manpower, material, and equipment shall be in the scope of contractor. SECI shall not provide any accommodation /Transportation for the employees of vendor. Everything has to be arranged by the contractor for his employees. | Should we need to provided Four Wheeler Camper for Owner's Personnel | Refer Amendment 01
27 | Technical Specifications | 15 of 26 | Section-VII | Water requirement for module cleaning arrangement and the cost for the same shall be borne by Contractor. The Contractor shall arrange for water on it’s own, by ensuring ESIA norms relevant government norms of Rajasthan for the use of water. | Please Clarify ESIA Norms | As per norms issued by MOEFCC & NABET
28 | Technical Specifications | 17 of 26 | Section-VII | AMC: Contractor shall enter into AMC contract with the OEM for the following items to cover requirements of maintenance and repairs. 1) Inverters 2) Inverter transformers 3) 33KV circuit breaker 4) 33KV instrument transformers (all CTs and VTs) 5) All types of meters and relays installed at 33KV level 6) SCADA 7) Transformers 8) Any other equipment as per plant requirement | Kindly Share all the Makes & Model Number of all the equipments | Refer Amendment 01
29 | Technical Specifications | 17 of 26 | Section-VII | The Employer shall maintain spares of major components | Please share the list of major spares available at site | Refer Amendment 01
30 | Technical Specifications | 24 of 26 | Section-VII | Guaranteed CUF: 21% | Please share the Basis / Calculation for the same. | Reference calculation for CUF for previous years is shown in Annexure 03 of the Amendment 01.
31 | Technical Specifications | 26 of 26 | Section-VII | Insurance Policy for 10 MW (AC) SPV plant at Badi Sid Rajasthan | Does Contractor has to take insurance based on the given IAR | As per the requirement mentioned in the SoW, Tender document.
32 |  |  |  |  | Please share following Site Details: 1) PVSyst report 2) Plant Array Layout 3) MMS Drawing Details 4) Solar Plant's DC & AC SLD 5) The actual PR value achieved year wise from COD date | Plant Array Layout and AC SLD is already provided.
33 | - | - | - | - | The Contractor's Liability should not be greater than 100% of Annual O&M Contract Value | Refer Amendment 01, Clause V SCC.
34 | - | - | - | - | We understand that "Machinery breakdown insurance" is in the scope of Employer Please clarify | No, it will be the responsibility of the contractor to take the insurance as per tender requirements
35 | - | - | - | - | Please share SLD, Plant Layout of Solar Plants till evacuation point | Already provided with the tender
36 | - | - | - | - | We understand that charges AMC of all Equipment's will be taken by Employer Kindly clarify | Refer Amendment 01.
37 | - | - | - | - | Maintaining Registrations & Regulatory approvals and its Liasoning fee is in the scope of Employer Please clarify | All the statutory payment shall be borne by Employer on reimbursement basis upon submission of valid Payment recipt (proof of payment) by the O&M contractor.
38 | - | - | - | - | Warranty of respective equipment is in the scope of Employer. The O&M Contractor shall extend the technical support for Warranty claims of respective equipment at Site level. Please clarify | Please refer the scope mentioned in the SoW and Amendment 01 of the tender document
39 | - | - | - | - | General - Taxes & Variation in Statutory Laws We understand that any change in Law/Statutory Laws after contract is awarded and its economic impact will be borne by Employer | The terms and conditions of the tender document shall prevail.Kindly refer the "Change in Law" clause of the tender document for the same.
40 | - | - | - | - | Kindly clarify the scope of providing internet & its charges | LAN is available at site. Any other internet conncetion if required at site, shall be arranged by the O&M contractor.
41 | - | - | - | - | Kindly clarify the scope of Internal Road maintenance in Solar Plant premises | Maintenance of Road within plant premises only.
42 | - | - | - | - | Security guards – the total members required is 10 nos inlcuidng gunman. Shall we consider 3 security guard (without ARM) per shift and one security with ARM in the night shift only. Is this OK | Noted. but the number of security staff per shift may vary depending upon the site requirement.
43 | - | - | - | - | Plant boundary has concrete compound wall and watch tower at all corners ? | The site premises is surrounded by wire fencing with temporary structure for security gaurds. The Contractor may visit the site to have better understanding on this.
44 | - | - | - | - | Kindly share the Make, model number and qty of CCTV – BOQ required | CCTV Make & Model =TVT & TVT/TD-9412E CCTV qty.= 03 nos.
45 | - | - | - | - | Kindly share Street light system make, model number and qty | Peripferal light Street Light Make & Model : 1. Bajaj & BRTFG 100 W LED 2: Qty no.= 66 nos Flood light: 1.OREVA & ORFLD-100 W Street light qty. = 20 Nos.
46 | - | - | - | - | Regarding OEM spares and OEM repair services – Hope no penalty charges is applicable, if OEM is not supplying the required spares on time or not deputing the technician on time. Kindly confirm | Please refer the scope mentioned in the SoW of the tender document
47 | - | - | - | - | Hope no penalty charges are applicable for non-availability of grid due to electricity authority schedule maintenance | Same will be considered under Grid outages based on the documentary evidence provided by the DISCOM/SLDC
48 | - | - | - | - | Insurance (page 26 of 26 Section VII TS) – whether we have to insure for INR 89.6 crores? (32 + 30 + 13.3 + 13.3 + 1 ) | Yes
49 | - | - | - | - | Hope PV module has 25 years of warranty and hence for any issue, Vikram solar shall supply PV modules to the site at free of cost. Kindly confirm | It will be dealt as per the Warrantee Terms and Conditions provided by the OEM of SPV Module.
50 | - | - | - | - | Regarding civil works and road maintenance – shall we estimate maximum of Rs. 5 lakhs per year for civil works and Rs. 10 lakhs per year for road maintenance. Kindly confirm | It will be the sole responsibility of the O&M contractor to estimate the price for the given contract
51 | - | - | - |  | Statutory payments (wages) – hope we have to follow Central wages. Kindly confirm | Bidders are required to make themselves aware regarding the State/Central Wages regulations and accordingly, the releavant statutary payments are to be made.
52 | - | - | - | - | Hope all statutory payments shall be paid by SECI. Kindly confirm | All the statutory payment shall be borne by Employer on reimbursement basis upon submission of valid Payment recipt (proof of payment) by the O&M contractor.

## Annexure 3
ANNEXURE 3
Monthly CUF data w.e.f. 01/04/2018 - 31/10/2022
YEAR | MONTH | NET Generation | Days / month | CUF
A | B | C | D | E = C /(10*10^3*(1-Df%*(n-1)*D*24) | Average PR From COD to till date
2018 | April | 1671360.3 | 30 | 23.21% | Year | PR%
2018 | May | 1722026.4 | 31 | 23.15% | 2016-17 | 83.1%
2018 | June | 1436131.2 | 30 | 19.95% | 2017-18 | 85.63%
2018 | July | 1566300.6 | 31 | 21.05% | 2018-19 | 81.57%
2018 | August | 1590617.4 | 31 | 21.38% | 2019-20 | 80.51%
2018 | September | 1639872.3 | 30 | 22.78% | 2020-21 | 83.13%
2018 | October | 1645258.8 | 31 | 22.11% | 2021-22 | 85.76%
2018 | November | 1426833.6 | 30 | 19.82% | 2022-23 | 82.72%
2018 | December | 1509221.1 | 31 | 20.29%
2019 | January | 1365744 | 31 | 18.36%
2019 | February | 1377640.5 | 28 | 20.5%
2019 | March | 1555494.3 | 31 | 20.91%
Total |  | 18506500.5 | 365 | 21.12%
2019 | April | 1740766.8 | 30 | 24.36%
2019 | May | 1791384 | 31 | 24.26%
2019 | June | 1639599.3 | 30 | 22.94%
2019 | July | 1531185 | 31 | 20.74%
2019 | August | 1459455.3 | 31 | 19.76%
2019 | September | 1612823.4 | 30 | 22.57%
2019 | October | 1638557.4 | 31 | 22.19%
2019 | November | 1197666 | 30 | 16.76%
2019 | December | 1417123.2 | 31 | 19.19%
2020 | January | 1418187 | 31 | 19.21%
2020 | February | 1620120.3 | 28 | 24.29%
2020 | March | 1697379.99 | 31 | 22.99%
Total |  | 18764247.69 | 365 | 21.6%
2020 | April | 1674533.4 | 30 | 23.43%
2020 | May | 1767721.5 | 31 | 23.94%
2020 | June | 1668732 | 30 | 23.35%
2020 | July | 1610488.5 | 31 | 21.81%
2020 | August | 1475441.1 | 31 | 19.98%
2020 | September | 1575970.2 | 30 | 22.05%
2020 | October | 1647725.1 | 31 | 22.31%
2020 | November | 1462671.9 | 30 | 20.47%
2020 | December | 1496045.4 | 31 | 20.26%
2021 | January | 1461065.7 | 31 | 19.79%
2021 | February | 1545178.1 | 28 | 23.17%
2021 | March | 1729062.6 | 31 | 23.42%
Total |  | 19114635.5 | 365 | 22%
2021 | April | 1782546.6 | 30 | 25.13%
2021 | May | 1661480.4 | 31 | 22.67%
2021 | June | 1659009.3 | 30 | 23.39%
2021 | July | 1533824.1 | 31 | 20.93%
2021 | August | 1682101.2 | 31 | 22.95%
2021 | September | 1361932.8 | 30 | 19.2%
2021 | October | 1693248.6 | 31 | 23.11%
2021 | November | 1439487.9 | 30 | 20.3%
2021 | December | 1238399.7 | 31 | 16.9%
2022 | January | 1413855 | 31 | 19.29%
2022 | February | 1587001.5 | 28 | 23.98%
2022 | March | 1812530.2 | 31 | 24.73%
Total |  | 18865417.3 | 365 | 21.88%
2022 | April | 1764422 | 30 | 25.07%
2022 | May | 1751916.9 | 31 | 24.09%
2022 | June | 1593786 | 30 | 22.65%
2022 | July | 1343090.7 | 31 | 18.47%
2022 | August | 1400137.8 | 31 | 19.25%
2022 | September | 1637039.7 | 30 | 23.26%
2022 | October | 1680155.7 | 31 | 23.1%
Total |  | 11170548.8 | 214 | 22.27%

## Annexure 4
ANNEXURE 4
List of Equipment for AMC
Name of the equipment | Unit Capacity | Quanity (Nos) | Make | Model
Inverters | 1 MW | 10 | ABB | PVS800-57- 1000KW-C
Power Transformer | 2 MVA | 5 | Electrotherm | ET 110011 to 110015
SCADA | NA | 1 | Greenwave
MB control (Telemetry data communication) | 10 MW | 1 | MB Control | MB15086
33KV circuit breaker (VCB) | 33 KV | 4 - Outdoor & 4 - Indoor | ABB | VD4/W36 12.32 / OVB-VBF 36.16.25
Any other equipment as per plant requirement